## Cover Page
PROCESS CONTROL TABLES - CRUSHING (F12)
KCGM GROWTH PROJECT
2000-F12-LST-PR-10001
NORTHERN STAR RESOURCES LIMITED
PRIMERO PROJECT NUMBER: 23517
DATE | REVISION | STATUS | PREPARED | REVIEWED | APPROVED
2024-07-15 | 0 | Issued for Design | J. Jones | E. Wilmot | D. Moltoni
2024-08-12 | 1 | Update PCT from IO list and contractor checks | JW. Ho | J. Jones | D. Moltoni
2024-10-24 | 2 | Reissued for Design | J. De Man | F. Chua | L. Stacey

## Revisions
PROCESS CONTROL TABLES
REVISION HISTORY
KCGM GROWTH PROJECT
2000-F12-LST-PR-10001
NORTHERN STAR RESOURCES LIMITED
Revision | Document Changes | Date
A for Sequence Flowchart Review Only | - Vendor Data TBC are highlighted yellow or in red text
| - Does not include the remainder of the Process Control Tables | 2023-12-12
B for Internal Review | - Vendor Data TBC are highlighted yellow or in red text
2024-04-02
C for Client Review | - Vendor Data TBC are highlighted yellow or in red text
2024-05-03
0 for Design | - Updated with Client Comments
| - Vendor Data TBC are highlighted yellow or in red text | 2024-07-15
1 for IO list updates | - Update against IO list and contractor checks
| - Vendor Data TBC are highlighted yellow or in red text | 2024-08-12
2 for Design | - Update against IO list and contractor checks
| - Vendor Data TBC / Holds are highlighted yellow or in red text | 2024-10-24

## TOC
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CRUSHING
2000-F12-LST-PR-10001
| Table of Contents |  |  | Total | Complete (%) | Alarms | Priority | Count | % | Abbreviations
| 1 | Analogue Inputs |  | 60 | 100 | 1 | Urgent (Critical Failure) | 9 | 100 | FC | Fail closed
| 2 | Analogue Outputs |  | 0 | 100 | 2 | High (Fault/Error) | 34 | 100 | FO | Fail open
| 3 | Digital Inputs |  | 164 | 100 | 3 | Low (Warning) | 59 | 100 | FL | Fail last
| 4 | Digital Outputs |  | 36 | 100 | 4 | Logging | 94 | 100 | LCP | Local control panel
| 5 | Totalisers |  | 1 | 100 | 5 | No Alarm | 14 | 100 | LCS | Local control station
| 6 | On/Off Valves |  | 9 | 100 |  | Total | 210 | 100 | A_Lo | Low alarm
| 7 | Control Valves |  | 1 | 100 |  |  |  |  | A_Hi | High alarm
| 8 | PID Controllers |  | 4 | 100 |  |  |  |  | A_LL | Low-Low alarm
| 9 | Drives & Interlocks |  | 39 | 100 |  |  |  |  | A_HH | High-High alarm
| 11 | Calculations |  | 8 | 100 |  |  |  |  | P_Lo | Low process switchpoint
| 12 | Misc. |  | 23 | 100 |  |  |  |  | P_Hi | High process switchpoint
|  |  | Total | 345 | 100 |  |  |  |  | P_LL | Low-Low process switchpoint
[10 empty] | P_HH | High-High process switchpoint
[10 empty] | OIT | Operator interface terminal
[10 empty] | Range | Instrument range
[10 empty] | SEQ | Sequence
[10 empty] | TBA | To be advised
[10 empty] | v | Vendor controlled
[10 empty] | VTA | Vendor to advise
[10 empty] | x | PCS controlled

## 1. Analogue Input
|  |  |  | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) |  | Range |  |  | Process Switchpoints | [11 empty] | Alarms
Area | Type | Loop No. | Suffix | [5 empty] | Trend (sec) | Min | Max | Unit | P_LL | P_LL Delay ON (sec) | P_LL Delay OFF (sec) | P_Lo | P_Lo Delay ON (sec) | P_Lo Delay OFF (sec) | P_Hi | P_Hi Delay ON (sec) | P_Hi Delay OFF (sec) | P_HH | P_HH Delay ON (sec) | P_HH Delay OFF (sec) | A_LL | A_LL Delay (sec) | A_Lo | A_Lo Delay (sec) | A_Hi | A_Hi Delay (sec) | A_HH | A_HH Delay (sec) | Alarm Masking Conditions | Comments | Rev
|  |  | X | ZT12005A | ZI12005A | 2000-F12-PID-PR-10001 | F12-BN-401 Rom Bin Truck 1 Parked Position Transmitter | F12BN401 Truck Pos. 1 | 1 | 0 | 30 | m |  |  |  | 3 | 5 |  | 14 | 5 | [6 empty] | 3 | 900 | [5 empty] | Process Value is the distance to ROM dump truck in metres P_Hi > sprays off: XV12005 AND XV12006 closed (Haul truck is in the 'OUT' or not dumping position) P_Lo < sprays on: XV12005 AND XV12006 open (Haul truck is in the 'IN' or dumping position) A_Lo = same as P_Lo but with a delay of 15 minutes to notify the CRO that sprays have been on for a long time (may indicate build up near the bump stop which is giving a false reading as the haul truck). NB: Process Switchpoints are based on CAT Haul Truck 793F dimensions (Length: 13.8m). Values to be confirmed during commissioning. | 0
|  |  | X | ZT12005B | ZI12005B | 2000-F12-PID-PR-10001 | F12-BN-401 Rom Bin Truck 2 Parked Position Transmitter | F12BN401 Truck Pos. 2 | 1 | 0 | 30 | m |  |  |  | 3 | 5 |  | 14 | 5 | [6 empty] | 3 | 900 | [5 empty] | Process Value is the distance to ROM dump truck in metres P_Hi > sprays off: XV12005 AND XV12006 closed (Haul truck is in the 'OUT' or not dumping position) P_Lo < sprays on: XV12005 AND XV12006 open (Haul truck is in the 'IN' or dumping position) A_Lo = same as P_Lo but with a delay of 15 minutes to notify the CRO that sprays have been on for a long time (may indicate build up near the bump stop which is giving a false reading as the haul truck). NB: Process Switchpoints are based on CAT Haul Truck 793F dimensions (Length: 13.8m). Values to be confirmed during commissioning. | 0
|  |  | X | LIT12200 | LI12200 | 2000-F12-PID-PR-10001 | F12-BN-405 Primary Crusher 2 Discharge Chamber Level Indicating Transmitter 1 | F12BN405 Disch Chamber 1 | 1 | 0 | 100 | % |  | 30 | 5 | 35 | 5 |  | 80 | 5 |  |  |  |  | 15 | 5 | 20 | 5 | 85 | 5 | 90 | 5 |  | P_Lo > Start F12-FA-401 (See Drives) P_Lo < Stop F12-FA-401 (See Drives) P_Hi > Acts as input to ROM traffic lights for haul truck dumping indication. Please see Digital Outputs. A_LL = Trip F12-FA-401 A_HH = Trip F12-CG-401 | 0
|  |  | X | LT12199 | LI12199 | 2000-F12-PID-PR-10001 | F12-BN-405 Primary Crusher 2 Discharge Chamber Level Indicating Transmitter 2 | F12BN405 Disch Chamber 2 | 1 | 0 | 100 | % | [6 empty] | 80 | 5 |  |  |  |  | 15 | 5 | 20 | 5 |  |  |  |  | Mask A_Lo and A_LoLo when LI12200 is healthy | LI12199 A_Lo and A_LL are to be aligned to LI12200 A_Lo and A_LL during commissioning (i.e. they need to be equivalent). Note that LE12199 is physically mounted lower than LE12200 in the Chamber. LE12199 is a backup for LE12200 to protect the apron feeder. P_Hi > Acts as input to ROM traffic lights for haul truck dumping indication. Please see Digital Outputs. A_LL = Trip F12-FA-401 | 0
|  |  | X | LT12004A | LI12004A | 2000-F12-PID-PR-10001 | F12-BN-401 Rom Bin Truck 1 Dump Pocket Level Transmitter | F12BN401 ROM Bin Lvl A | 1 | 0 | 100 | % | [6 empty] | 70 | 5 | [8 empty] | 80 | 5 |  |  |  | Dump pocket transmitter. Acts as input to ROM traffic lights for haul truck dumping indication. Please see Digital Outputs. Values to be determined during commissioning. | 0
|  |  | X | LT12004B | LI12004B | 2000-F12-PID-PR-10001 | F12-BN-401 Rom Bin Truck 2 Dump Pocket Level Transmitter | F12BN401 ROM Bin Lvl B | 1 | 0 | 100 | % | [6 empty] | 70 | 5 | [8 empty] | 80 | 5 |  |  |  | Dump pocket transmitter. Acts as input to ROM traffic lights for haul truck dumping indication. Please see Digital Outputs. Values to be determined during commissioning. | 0
|  |  |  | SE12059 | SI12059 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher 2 Countershaft Speed Sensor | F12CG401 C/Shaft | 1 | 0 | 600 | RPM | [12 empty] | 100 | 5 | 120 | 5 |  |  |  |  | Mask when F12-CG-401 is Not Running. | Frequency Transducer fitted. A_LL < Trip F12-CG-401 Alarm setpoints and range from 2000-ME001.1-F17-50001. | 2
|  |  |  | SE12060 | SI12060 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher 2 Main Shaft Speed Sensor | F12CG401 M/Shaft | 1 | 0 | 600 | RPM | [16 empty] | 20 | 5 |  |  | Mask when F12-CG-401 is Not Running. | Frequency Transducer fitted. Alarm setpoints and range from 2000-ME001.1-F12-50001. | B
|  |  | X | ZT12061 | ZI12061 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher 2 Mantle Position Transmitter | F12CG401 Mantle Pos Phys | 1 | 0 | 457 | mm | [16 empty] | 450 | 5 |  |  |  | This inputs into F12CALC10007 to better represent the Crusher Mantle Position. The output of F12CALC10007 inputs into ZIC12062. A_Hi = Warning. | 0
|  |  | X | FIT12079 | FI12079 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher 2 Dust Seal Blower Discharge Flow Indicating Transmitter | F12BW401 Seal Blower | 1 | 0 | 85 | m3/hr | [12 empty] | 34 | 5 | 60 | 5 |  |  |  |  | Mask when F12-CG-401 is Not Running and F12-BW-401 is Not Running | As per FLS I/O List 2000-ME001.1-F17-50001. A_LL = Trip F12-CG-401 | 0
|  |  | X | VT12057 | VI12057 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher Drive Motor Main Drive Bearing DE Vibration Transmitter | F12CG401 Mtr D/E Brg | 1 | 0 | 12.5 | mm/s | [16 empty] | 3 | 5 | 5 | 5 |  | As per FLS I/O List 2000-ME001.1-F17-50001. A_HH = Trip F12-CG-401 A_Hi = Warning Weq motor datasheet vibration (nominal): 2.3 mm/s 2000-ME001.1-C05-50001 | 0
|  |  | X | VT12058 | VI12058 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher Drive Motor Main Drive Bearing NDE Vibration Transmitter | F12CG401 Mtr NDE Brg | 1 | 0 | 12.5 | mm/s | [16 empty] | 3 | 5 | 5 | 5 |  | As per FLS I/O List 2000-ME001.1-F17-50001. A_HH = Trip F12-CG-401 A_Hi = Warning Weq motor datasheet vibration (nominal): 2.3 mm/s 2000-ME001.1-C05-50001 | 0
|  |  |  | VT12069 | VI12069 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher Assembly Countershaft Vibration Transmitter 1 | F12CG401 C/Shaft 1 | 1 | 0 | 12.5 | mm/s | [21 empty] | As per FLS I/O List 2000-ME001.1-F17-50001. | C
|  |  |  | VT12070 | VI12070 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher Assembly Countershaft Vibration Transmitter 2 | F12CG401 C/Shaft 2 | 1 | 0 | 12.5 | mm/s | [21 empty] | As per FLS I/O List 2000-ME001.1-F17-50001. | C
|  |  | X | TIT12064 | TI12064 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher Assembly Outer Eccentric Upper Temperature Transmitter | F12CG401 Outr Ecc Upper | 1 | -5 | 100 | ℃ | [16 empty] | 54 | 5 | 60 | 5 |  | As per FLS I/O List 2000-ME001.1-F17-50001. A_HH to be set during commissioning. A_HH = Trip F12-CG-401 | 2
|  |  | X | TIT12065 | TI12065 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher Assembly Outer Eccentric Wear Ring Temperature Transmitter | F12CG401 Outr Ecc Ring | 1 | -5 | 100 | ℃ | [16 empty] | 54 | 5 | 60 | 5 |  | As per FLS I/O List 2000-ME001.1-F17-50001. A_HH to be set during commissioning. A_HH = Trip F12-CG-401 | 2
|  |  | X | TIT12066 | TI12066 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher Assembly Outer Eccentric Lower Temperature Transmitter | F12CG401 Outr Ecc Lower | 1 | -5 | 100 | ℃ | [16 empty] | 54 | 5 | 60 | 5 |  | As per FLS I/O List 2000-ME001.1-F17-50001. A_HH to be set during commissioning. A_HH = Trip F12-CG-401 | 2
|  |  | X | TIT12067 | TI12067 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher Assembly Countershaft Outboard Bearing Temperature Transmitter | F12CG401 C/Shaft OB Brg | 1 | -5 | 100 | ℃ | [16 empty] | 54 | 5 | 60 | 5 |  | As per FLS I/O List 2000-ME001.1-F17-50001. A_HH to be set during commissioning. A_HH = Trip F12-CG-401 | 2
|  |  | X | TIT12068 | TI12068 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher Assembly Countershaft Inboard Bearing Temperature Transmitter | F12CG401 C/Shaft IB Brg | 1 | -5 | 100 | ℃ | [16 empty] | 54 | 5 | 60 | 5 |  | As per FLS I/O List 2000-ME001.1-F17-50001. A_HH to be set during commissioning. A_HH = Trip F12-CG-401 | 2
|  |  | X | FIT12071 | FI12071 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher Assembly Outer Eccentric Lube Flow Indicating Transmitter | F12CG401 Outer Ecc Lube | 1 | 0 | 200 | LPM | [12 empty] | 50 | 5 | 86 | 5 |  |  |  |  | Mask when F12-PO-404/405 is Not Running | As per FLS I/O List 2000-ME001.1-F17-50001. A_LL = Trip F12-CG-401 | 0
|  |  | X | FIT12072 | FI12072 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher Assembly Upper Eccentric Lube Flow Indicating Transmitter | F12CG401 Upper Ecc. Lube | 1 | 0 | 25 | LPM | [12 empty] | 7.5 | 5 | 13.5 | 5 |  |  |  |  | Mask when F12-PO-404/405 is Not Running | As per FLS I/O List 2000-ME001.1-F17-50001. A_LL = Trip F12-CG-401 | 0
|  |  | X | FIT12073 | FI12073 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher Assembly Pinion Lube Flow Indicating Transmitter | F12CG401 Pinion Lube | 1 | 0 | 25 | LPM | [12 empty] | 7.5 | 5 | 13.5 | 5 |  |  |  |  | Mask when F12-PO-404/405 is Not Running | As per FLS I/O List 2000-ME001.1-F17-50001. A_LL = Trip F12-CG-401 | 0
|  |  | X | FIT12074 | FI12074 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher Assembly Countershaft Supply Flow Indicating Transmitter | F12CG401 C/Shaft Lube | 1 | 0 | 25 | LPM | [12 empty] | 7.5 | 5 | 13.5 | 5 |  |  |  |  | Mask when F12-PO-404/405 is Not Running | As per FLS I/O List 2000-ME001.1-F17-50001. A_LL = Trip F12-CG-401 | 0
|  |  | X | FIT12075 | FI12075 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher Assembly Inner Eccentric Supply Flow Indicating Transmitter | F12CG401 Inner Ecc. Lube | 1 | 0 | 200 | LPM | [12 empty] | 50 | 5 | 86 | 5 |  |  |  |  | Mask when F12-PO-404/405 is Not Running | As per FLS I/O List 2000-ME001.1-F17-50001. A_LL = Trip F12-CG-401 | 0
|  |  |  | TIT12080 | TI12080 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Hydraulic Oil Reservoir Temperature Transmitter | F12LU401 Hyd Oil Resvr | 1 | 0 | 100 | ℃ |  |  |  | 32 | 5 |  | 38 | 5 |  |  |  |  | 21 | 5 | 27 | 5 |  |  | 60 | 5 |  | As per FLS I/O List 2000-ME001.1-F17-50001. P_Hi >= Stops F12-HT-417/418 P_Lo <= Starts F12-HT-417/418 A_LL = Trip F12-PO-403/410 A_HH = Trip F12-PO-403/410 and F12-HT-417/418 | 2
|  |  |  | PT12091 | PI12091 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher 2 Hydraulic System Accumulator Pressure Transmitter | F12CG401 Hydraulic MPS | 1 | 0 | 27580 | kPa | [21 empty] | Hydraulic System Mantle Accumulator. Source: 2000-ME001.1-F17-50001 | 2
|  |  |  | TIT12110 | TI12110 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Lube Oil Reservoir Temperature Transmitter | F12LU401 Lube Tank | 1 | -5 | 100 | ℃ |  |  |  | 32 | 5 |  | 30 | 5 |  | 38 | 5 |  | 21 | 5 | 27 | 5 | 60 | 5 |  |  |  | TIC12110 switches Primary Crusher 2 Lubrication System Heaters 1, 2, 3 and 4 On/Off based on the set point. P_HiHi >= Stops F12-HT-407/408/409/410 P_Lo <= Starts F12-HT-407/408/409/410 A_Hi = Trips F12-HT-407/408/409/410 P_Hi = No alarm, start permissive F12-PO-404/5 A_Lo = Warning A_LL = Trip F12-PO-404/405, please see Drives sheet. 32C and 38C switchpoints from 2000-ME001.1-F17-50001. | 2
|  |  |  | PIT12118 | PI12118 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Pump Common Discharge Pressure Indicating Transmitter | F12PO404/405 Discharge | 1 | 0 | 2760 | kPa | [16 empty] | 727 | 5 |  |  |  | As per FLS Instrument List 2000-ME001.1-F16-50001 and IO List 2000-ME001.1-F17-50001. A_Hi = Warning | 1
|  |  |  | TIT12128 | TI12128 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Lube Oil Return Temperature Transmitter | F12LU401 Lube Return | 1 | -5 | 100 | ℃ |  |  |  | 40 | 5 | [11 empty] | 55 | 5 | 60 | 5 |  | As per FLS I/O List 2000-ME001.1-F17-50001 A_HH = Trip F12-CG-401 | 2
|  |  |  | F12CALC0001 | TDI12128 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Lube Oil Return Temperature Differential | F12LU401 Rtrn Lube Diff | 1 | -20 | 20 | ℃ | [22 empty] | B
|  |  | X | WIT12097 | WI12097 | 2000-F12-PID-PR-10001 | F12-LU-402 Primary Crusher 2 Spider Lubrication System Lube Tank Weight Indicating Transmitter | F12LU402 Grease Drum | 1 | 0 | 440 | kg | [14 empty] | 44 | 5 | [5 empty] | As per FLS I/O List 2000-ME001.1-F17-50001. | 2
|  |  |  | VT12507A | VI12507A | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Drive Pulley Vibration Transmitter 1 | F12CV401 Pulley1 | 1 | 0 | 12.5 | mm/s | [16 empty] | 1 | 5 | 2 | 5 |  | A_HH = Trip F12CV401 A_Hi = Warning Alarm setpoints to be confirmed during commissioning. | 0
|  |  |  | TT12507A | TI12507A | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Drive Pulley Temperature Transmitter 1 | F12CV401 Pulley1 | 1 | -30 | 80 | ℃ | [10 empty] | N | [5 empty] | 60 | 5 | 70 | 5 |  | A_HH = Trip F12CV401 A_Hi = Warning Alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | VT12560A | VI12560A | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Drive Pulley Vibration Transmitter 1 | F12CV402 Pulley1 | 1 | 0 | 12.5 | mm/s | [16 empty] | 1 | 5 | 2 | 5 |  | A_HH = Trip F12CV402 A_Hi = Warning Alarm setpoints to be confirmed during commissioning. | 0
|  |  |  | TT12560A | TI12560A | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Drive Pulley Temperature Transmitter 1 | F12CV402 Pulley1 | 1 | -30 | 80 | ℃ | [16 empty] | 60 | 5 | 70 | 5 |  | A_HH = Trip F12CV402 A_Hi = Warning Alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | PDIT12542 | PDI12542 | 2000-F12-PID-PR-10002 | F12-DC-401 Primary Crusher 2 Dust Collector Air Chambers Differential Pressure Indicating Transmitter | F12DC401 Pressure Delta | 1 | 0 | 2500 | Pa | [12 empty] | 300 | 5 | 800 | 5 | 1300 | 5 | 1800 | 5 | Mask if F12DC401 Not Running | A_HH for more than 1 hour = Trip F12DC401 A_Hi = Logging Event (pulse cleaning started by Dust Collector Controller) A_Lo = Logging Event (pulse cleaning stopped by Dust Collector Controller) A_LL = Warning (investigate F12DC401 and PDIT for faults) | 1
|  |  |  | UT12010 | UI12010 | 2000-F12-PID-PR-10001 | F12-SR-001 Primary Crushing 11kV Switchroom Temperature/Humidity Transmitter | F12 11kV Switchroom | 1 | -5 | 80 | ℃ | [16 empty] | 30 | 5 |  |  |  | A_Hi = Alarm. Nominal 24C. Alarm setpoint to be confirmed during commissioning. | 2
|  |  |  | UT12011 | UI12011 | 2000-F12-PID-PR-10001 | F12-SR-002 Primary Crushing 415V Switchroom Temperature/Humidity Transmitter | F12 415V Switchroom | 1 | -5 | 80 | ℃ | [16 empty] | 30 | 5 |  |  |  | A_Hi = Alarm. Nominal 24C. Alarm setpoint to be confirmed during commissioning. | 2
|  |  |  | UT12012 | UI12012 | 2000-F12-PID-PR-10001 | F12-SR-002 Primary Crushing 415V Switchroom Transformer Enclosure Temperature/Humidity Transmitter | F12 415V MCC Transf Room | 1 | -5 | 80 | ℃ | [16 empty] | 30 | 5 |  |  |  | A_Hi = Alarm. Nominal 24C. Alarm setpoint to be confirmed during commissioning. | 2
|  |  |  | PT12392 | PI12392 | 2000-F24-PID-PR-10012 | F12-RA-407 Primary Crushing Air Receiver Outlet Pressure Indicating Transmitter | F12RA407 Outlet Pressure | 1 | 0 | 1100 | kPa(g) | [14 empty] | 600 | 5 | 1000 | 5 |  |  | Mask A_Lo alarm when F24-CM-401, 402 AND 403 are stopped Mask A_Lo for 30 seconds during start up. | A_Hi = Warning A_Lo = Warning Normal operating = 9.8 bar Maximum operating pressure = 10 bar Minimum system outlet pressure = 6 bar Nominal values and alarm setpoints to be confirmed during commissioning | 1
|  |  |  | LT13002 | LI13002 | 2000-F13-PID-PR-10001 | F12-SKP-401 Coarse Ore Stockpile 2 Level Transmitter | F12SKP401 Stockpile 2 | 1 | 0 | 100 | % | [12 empty] | 20 | 5 | 30 | 5 | 80 | 5 | 90 | 5 |  | A_HH =Trip F12-CV-401 AND 402. A_Hi = Trip F12-FA-401 A_Lo = Warning A_LL = Trip F13-FA-411/412 Alarm setpoints to be confirmed during commissioning. | 0
|  |  |  | TE12580A | TI12580A | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Motor Phase U RTD | F12CV401 Mtr Phase U RTD | 1 | -20 | 200 | ℃ | [16 empty] | 140 | 5 | 150 | 5 |  | A_Hi = Warning A_HH = Trip Conveyor Drive. Source: 2000-ME050-F14-10001. | 0
|  |  |  | TE12580B | TI12580B | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Motor Phase V RTD | F12CV401 Mtr Phase V RTD | 1 | -20 | 200 | ℃ | [16 empty] | 140 | 5 | 150 | 5 |  | A_Hi = Warning A_HH = Trip Conveyor Drive. Source: 2000-ME050-F14-10001. | 0
|  |  |  | TE12580C | TI12580C | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Motor Phase W RTD | F12CV401 Mtr Phase W RTD | 1 | -20 | 200 | ℃ | [16 empty] | 140 | 5 | 150 | 5 |  | A_Hi = Warning A_HH = Trip Conveyor Drive. Source: 2000-ME050-F14-10001. | 0
|  |  |  | TE12580D | TI12580D | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Motor DE Bearing RTD | F12CV401 Mtr DE Bearing | 1 | -20 | 200 | ℃ | [16 empty] | 90 | 5 | 95 | 5 |  | A_Hi = Warning A_HH = Trip Conveyor Drive. Source: 2000-ME050-F14-10001. | 0
|  |  |  | TE12580E | TI12580E | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Motor NDE Bearing RTD | F12CV401 Mtr NDE Bearing | 1 | -20 | 200 | ℃ | [16 empty] | 90 | 5 | 95 | 5 |  | A_Hi = Warning A_HH = Trip Conveyor Drive. Source: 2000-ME050-F14-10001. | 0
|  |  |  | TE12581A | TI12581A | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Motor Phase U RTD | F12CV402 Mtr Phase U RTD | 1 | -20 | 200 | ℃ | [16 empty] | 140 | 5 | 150 | 5 |  | A_Hi = Warning A_HH = Trip Conveyor Drive. Source: 2000-ME050-F14-10001. | 0
|  |  |  | TE12581B | TI12581B | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Motor Phase V RTD | F12CV402 Mtr Phase V RTD | 1 | -20 | 200 | ℃ | [16 empty] | 140 | 5 | 150 | 5 |  | A_Hi = Warning A_HH = Trip Conveyor Drive. Source: 2000-ME050-F14-10001. | 0
|  |  |  | TE12581C | TI12581C | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Motor Phase W RTD | F12CV402 Mtr Phase W RTD | 1 | -20 | 200 | ℃ | [16 empty] | 140 | 5 | 150 | 5 |  | A_Hi = Warning A_HH = Trip Conveyor Drive. Source: 2000-ME050-F14-10001. | 0
|  |  |  | TE12581D | TI12581D | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Motor DE Bearing RTD | F12CV402 Mtr DE Bearing | 1 | -20 | 200 | ℃ | [16 empty] | 90 | 5 | 95 | 5 |  | A_Hi = Warning A_HH = Trip Conveyor Drive. Source: 2000-ME050-F14-10001. | 0
|  |  |  | TE12581E | TI12581E | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Motor NDE Bearing RTD | F12CV402 Mtr NDE Bearing | 1 | -20 | 200 | ℃ | [16 empty] | 90 | 5 | 95 | 5 |  | A_Hi = Warning A_HH = Trip Conveyor Drive. Source: 2000-ME050-F14-10001. | 0
|  |  |  | LIT12260 | LI12260 | 2000-F12-PID-PR-10003 | F12-TK-423 Primary Crusher 2 Cooling Water Tank Level Indicating Transmitter | F12TK423 Cooling Water | 1 | 0 | 100 | % |  |  |  | 35 | 5 |  | 75 | 5 |  |  |  |  | 20 | 5 | 30 | 5 | 80 | 5 |  |  |  | A_Hi = Warning A_Lo = Warning A_LL = Trip Duty Pump F12-PW-425/426 Process switchpoints opening and closing XV12259 when valve is placed in auto. Nominal values and alarm setpoints to be confirmed during commissioning | 0
|  |  |  | TIT12261 | TI12261 | 2000-F12-PID-PR-10003 | F12-TK-423 Primary Crusher 2 Cooling Water Tank Temperature Indicating Transmitter | F12TK423 Cooling Water | 1 | -5 | 100 | ℃ | [16 empty] | 30 | 5 |  |  | Mask when F12-PW-425 AND 426 Not Running | Primary Crusher 2 Chiller designed for entering water temperature of 25C. A_Hi = Warning | 2
|  |  |  | TIT12267 | TI12267 | 2000-F12-PID-PR-10003 | F12-CU-401 Primary Crusher 2 Chiller Outlet Cooling Water Temperature Indicating Transmitter | F12CU401 Outlet Water | 1 | -5 | 100 | ℃ | [16 empty] | 20 | 5 |  |  | Mask when F12-PW-425 AND 426 Not Running | Primary Crusher 2 Chiller designed to cool water to 18C. A_Hi = Warning | 2
|  |  |  | TE12228 | TI12228 | 2000-F12-PID-PR-10001 | F12-FA-401 Primary Crusher 2 Discharge Apron Feeder Gearboox Sump RTD | F12FA401 Gearbox Sump | 1 | -50 | 200 | ℃ | [6 empty] | 70 | 5 | [10 empty] | 90 | 5 |  | Gearbox Sump Cooler Temperature Element. A_HH = Alarm to signify overloading of gearbox and feeder F12FA401 trip. P_Hi = Start permissive for F12FA401 drive. | 1
|  |  |  | TE12229 | TI12229 | 2000-F12-PID-PR-10001 | F12-FA-401 Primary Crusher 2 Discharge Apron Feeder Gearboox High Speed Bearing RTD | F12FA401 Gearbox Bearing | 1 | -50 | 200 | ℃ | [16 empty] | 60 | 5 | 90 | 5 |  | Gearbox High Speed Bearing Temperature Element. A_Hi = Warning A_HH = F12FA401 trip. | 0
|  |  |  | VT12507B | VI12507B | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Drive Pulley Vibration Transmitter 2 | F12CV401 Pulley2 | 1 | 0 | 12.5 | mm/s | [16 empty] | 1 | 5 | 2 | 5 |  | A_HH = Trip F12CV401 A_Hi = Warning Alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | TT12507B | TI12507B | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Drive Pulley Temperature Transmitter 2 | F12CV401 Pulley2 | 1 | -30 | 80 | ℃ | [16 empty] | 60 | 5 | 70 | 5 |  | A_HH = Trip F12CV401 A_Hi = Warning Alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | VT12560B | VI12560B | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Drive Pulley Vibration Transmitter 2 - Vibration | F12CV402 Pulley2 | 1 | 0 | 12.5 | mm/s | [16 empty] | 1 | 5 | 2 | 5 |  | A_HH = Trip F12CV402 A_Hi = Warning Alarm setpoints to be confirmed during commissioning. | 1
|  |  |  | TT12560B | TI12560B | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Drive Pulley Vibration Transmitter 2 - Temperature | F12CV402 Pulley2 | 1 | -30 | 80 | ℃ | [16 empty] | 60 | 5 | 70 | 5 |  | A_HH = Trip F12CV402 A_Hi = Warning Alarm setpoints to be confirmed during commissioning. | 1
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 60 | 60

## 2. Analogue Output
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CRUSHING
2000-F12-LST-PR-10001
ANALOGUE OUTPUT
|  |  |  | Tag Source | Tag Name | P&ID | Abbreviated Description (Faceplate) |  | Range
Area | Type | Loop No. | Suffix |  |  |  |  | Trend (sec) | Min | Max | Unit | Comments | Rev
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 0 | 0
Update PCT from IO list and contractor checks

## 4. Digital Output
KCGM GROWTH PROJECT
|  |  |  | PROCESS CONTROL TABLES - CRUSHING |  |  |  | *SOFTWARE DEBOUNCE IS REQUIRED ON ALL DIGITAL INSTRUMENTS (NO HARDWARE DEBOUNCE)*
2000-F12-LST-PR-10001
DIGITAL INSTRUMENTS (DO)
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) | State 0 | State 1 | Alarm State | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev
|  |  | X | YI12000A | XI12000A | 2000-F12-PID-PR-10001 | F12-BN-401 Rom Bin Truck 1 Dump Pocket (Red) Traffic Light 1 | ROM Bin P1 Light 1A | Off | On |  |  |  | XI12000A = Off and XI12000B = On, green (dump). XI12000A = On and XI12000B = Off, red (no dump). Green light when: F12-CG-401 = RUNNING. SE and NW radar transmitter and traffic light positioning to be confirmed during commissioning. IF(F12-CG-401 == RUNNING AND HEALTHY AND LI12200 < P_Hi AND LI12199 < P_Hi AND LAH12201 NORMAL AND ZI12005B > P_Hi AND LI12004A < P_Hi AND LI12004B < P_Hi AND 12CG401_T2 NOT STARTED AND XI12019D HOME) == TRUE, THEN: XI12000A == OFF AND XI12000B ==ON (SET TO GREEN) ELSE XI12000A == ON AND XI12000B ==OFF (SET TO RED) TBC Park Position digital input for Rock Breaker package. | 2
|  |  |  | YI12000B | XI12000B | 2000-F12-PID-PR-10002 | F12-BN-401 Rom Bin Truck 1 Dump Pocket (Green) Traffic Light 1 | ROM Bin P1 Light 1B | Off | On |  |  |  | XI12000A = Off and XI12000B = On, green (dump). XI12000A = On and XI12000B = Off, red (no dump). Green light when: F12-CG-401 = RUNNING. SE and NW radar transmitter and traffic light positioning to be confirmed during commissioning. IF(F12-CG-401 == RUNNING AND HEALTHY AND LI12200 < P_Hi AND LI12199 < P_Hi AND LAH12201 NORMAL AND ZI12005B > P_Hi AND LI12004A < P_Hi AND LI12004B < P_Hi AND 12CG401_T2 NOT STARTED AND XI12019D HOME) == TRUE, THEN: XI12000A == OFF AND XI12000B == ON (SET TO GREEN) ELSE XI12000A == ON AND XI12000B ==OFF (SET TO RED) TBC Park Position digital input for Rock Breaker package. | 2
|  |  | X | YI12001A | XI12001A | 2000-F12-PID-PR-10001 | F12-BN-401 Rom Bin Truck 1 Dump Pocket (Red) Traffic Light 2 | ROM Bin P1 Light 2A | Off | On |  |  |  | XI12001A = Off and XI12001B = On, green (dump). XI12001A = On and XI12001B = Off, red (no dump). Green light when: F12-CG-401 = RUNNING. SE and NW radar transmitter and traffic light positioning to be confirmed during commissioning. IF(F12-CG-401 == RUNNING AND HEALTHY AND LI12200 < P_Hi AND LI12199 < P_Hi AND LAH12201 NORMAL AND ZI12005B > P_Hi AND LI12004A < P_Hi AND LI12004B < P_Hi AND 12CG401_T2 NOT STARTED AND XI12019D HOME AND ZI12005A > P_Hi) == TRUE, THEN: XI12001A == OFF AND XI12001B == ON (SET TO GREEN) ELSE XI12001A == ON AND XI12001B ==OFF (SET TO RED) TBC Park Position digital input for Rock Breaker package. | 2
|  |  |  | YI12001B | XI12001B | 2000-F12-PID-PR-10001 | F12-BN-401 Rom Bin Truck 1 Dump Pocket (Green) Traffic Light 2 | ROM Bin P1 Light 2B | Off | On |  |  |  | XI12001A = Off and XI12001B = On, green (dump). XI12001A = On and XI12001B = Off, red (no dump). Green light when: F12-CG-401 = RUNNING. SE and NW radar transmitter and traffic light positioning to be confirmed during commissioning. IF(F12-CG-401 == RUNNING AND HEALTHY AND LI12200 < P_Hi AND LI12199 < P_Hi AND LAH12201 NORMAL AND ZI12005B > P_Hi AND LI12004A < P_Hi AND LI12004B < P_Hi AND 12CG401_T2 NOT STARTED AND XI12019D HOME AND ZI12005A > P_Hi) == TRUE, THEN: XI12001A == OFF AND XI12001B == ON (SET TO GREEN) ELSE XI12001A == ON AND XI12001B ==OFF (SET TO RED) TBC Park Position digital input for Rock Breaker package. | 2
|  |  | X | YI12002A | XI12002A | 2000-F12-PID-PR-10001 | F12-BN-401 Rom Bin Truck 2 Dump Pocket (Red) Traffic Light 1 | ROM Bin P2 Light 1A | Off | On |  |  |  | XI12002A = Off and XI12002B = On, green (dump). XI12002A = On and XI12002B = Off, red (no dump). Green light when: F12-CG-401 = RUNNING. SE and NW radar transmitter and traffic light positioning to be confirmed during commissioning. IF(F12-CG-401==RUNNING AND HEALTHY AND F12-LI-12200 < P_Hi AND LI12199 < P_Hi AND LAH12201 NORMAL AND ZI12005A > P_Hi AND LI12004A < P_Hi AND LI12004B < P_Hi AND 12CG401_T2 NOT STARTED AND XI12019D ACTIVE) == TRUE, THEN: XI12002A == OFF AND XI12002B == ON (SET TO GREEN) ELSE XI12002A == ON AND XI12002B ==OFF (SET TO RED) TBC Park Position digital input for Rock Breaker package. | 2
|  |  |  | YI12002B | XI12002B | 2000-F12-PID-PR-10001 | F12-BN-401 Rom Bin Truck 2 Dump Pocket (Green) Traffic Light 1 | ROM Bin P2 Light 1B | Off | On |  |  |  | XI12002A = Off and XI12002B = On, green (dump). XI12002A = On and XI12002B = Off, red (no dump). Green light when: F12-CG-401 = RUNNING. SE and NW radar transmitter and traffic light positioning to be confirmed during commissioning. IF(F12-CG-401==RUNNING AND HEALTHY AND F12-LI-12200 < P_Hi AND LI12199 < P_Hi AND LAH12201 NORMAL AND ZI12005A > P_Hi AND LI12004A < P_Hi AND LI12004B < P_Hi AND 12CG401_T2 NOT STARTED AND XI12019D ACTIVE) == TRUE, THEN: XI12002A == OFF AND XI12002B == ON (SET TO GREEN) ELSE XI12002A == ON AND XI12002B ==OFF (SET TO RED) TBC Park Position digital input for Rock Breaker package. | 2
|  |  | X | YI12003A | XI12003A | 2000-F12-PID-PR-10001 | F12-BN-401 Rom Bin Truck 2 Dump Pocket (Red) Traffic Light 2 | ROM Bin P2 Light 2A | Off | On |  |  |  | XI12003A = Off and XI12003B = On, green (dump). XI12003A = On and XI12003B = Off, red (no dump). Green light when: F12-CG-401 = RUNNING. SE and NW radar transmitter and traffic light positioning to be confirmed during commissioning. IF(F12-CG-401== RUNNING AND HEALTHY AND F12-LI-12200 < P_Hi AND LI12199 < P_Hi AND LAH12201 NORMAL AND ZI12005A > P_Hi AND LI12004A < P_Hi AND LI12004B < P_Hi AND 12CG401_T2 NOT STARTED AND XI12019D ACTIVE AND ZI12005B > P_Hi) == TRUE, THEN: XI12003A == OFF AND XI12003B == ON (SET TO GREEN) ELSE XI12003A == ON AND XI12003B ==OFF (SET TO RED) TBC Park Position digital input for Rock Breaker package. | 2
|  |  |  | YI12003B | XI12003B | 2000-F12-PID-PR-10001 | F12-BN-401 Rom Bin Truck 2 Dump Pocket (Green) Traffic Light 2 | ROM Bin P2 Light 2B | Off | On |  |  |  | XI12003A = Off and XI12003B = On, green (dump). XI12003A = On and XI12003B = Off, red (no dump). Green light when: F12-CG-401 = RUNNING. SE and NW radar transmitter and traffic light positioning to be confirmed during commissioning. IF(F12-CG-401== RUNNING AND HEALTHY AND F12-LI-12200 < P_Hi AND LI12199 < P_Hi AND LAH12201 NORMAL AND ZI12005A > P_Hi AND LI12004A < P_Hi AND LI12004B < P_Hi AND 12CG401_T2 NOT STARTED AND XI12019D ACTIVE AND ZI12005B > P_Hi) == TRUE, THEN: XI12003A == OFF AND XI12003B == ON (SET TO GREEN) ELSE XI12003A == ON AND XI12003B ==OFF (SET TO RED) TBC Park Position digital input for Rock Breaker package. | 2
|  |  | X | YY12050 | YA12050 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher 2 Primary Crusher 2 Surge Bin Start Siren | F12CG401 Start Siren | Off | On |  |  |  | Siren is activated for 15 secs before drive (F12-CG-401) is allowed to start. | 2
|  |  |  | XY12137 | XI12137 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Control Panel Hydraulic Pump 1 Running Indicator Light | F12PO403 Pump 1 Running | Stopped | Running |  |  |  |  | 2
|  |  |  | XY12138 | XI12138 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Control Panel Hydraulic Pump 2 Running Indicator Light | F12PO410 Pump 2 Running | Stopped | Running |  |  |  |  | 2
|  |  |  | XY12139 | XI12139 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Control Panel Lubrication Pump 1 Running Indicator Light | F12PO404 Pump 1 Running | Stopped | Running |  |  |  |  | 2
|  |  |  | XY12140 | XI12140 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Control Panel Lubrication Pump 2 Running Indicator Light | F12PO405 Pump 2 Running | Stopped | Running |  |  |  |  | 2
|  |  |  | YY12223 | YA12223 | 2000-F12-PID-PR-10001 | F12-FA-401 Primary Crusher 2 Discharge Apron Feeder Start Siren | F12FA401 Start Siren | Off | On |  |  |  | Siren is activated for 15 secs before drive is allowed to start | 2
|  |  |  | YY12505A | YA12505A | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Tail End Start Siren | F12CV401 T/E Start Siren | Off | On |  |  |  | Siren is activated for 15 secs before drive is allowed to start | 2
|  |  |  | YY12505B | YA12505B | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Head End Start Siren | F12CV401 H/E Start Siren | Off | On |  |  |  | Siren is activated for 15 secs before drive is allowed to start | 2
|  |  |  | YY12505C | YA12505C | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Mid End Start Siren | F12CV401 M/E Start Siren | Off | On |  |  |  | Siren is activated for 15 secs before drive is allowed to start | 2
|  |  |  | YY12559A | YA12559A | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Tail End Start Siren | F12CV402 T/E Start Siren | Off | On |  |  |  | Siren is activated for 15 secs before drive is allowed to start | 2
|  |  |  | YY12559B | YA12559B | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Head End Start Siren | F12CV402 H/E Start Siren | Off | On |  |  |  | Siren is activated for 15 secs before drive is allowed to start | 2
|  |  |  | YY12234A | YA12234A | 2000-F12-PID-PR-10001 | F12-FN-410 Primary Crusher 2 Buried Vault Ventilation Fan ROM Entrance Warning Beacon | F12FN410 Beacon 1 | Off | On |  |  |  | Activate bit when F12-FN-410 is Not Running. Will electrically activate local beacon within ROM tunnel. | 2
|  |  |  | YY12234B | YA12234B | 2000-F12-PID-PR-10001 | F12-FN-410 Primary Crusher 2 Buried Vault Ventilation Fan CV401 Tunnel Entrance 1 Warning Beacon | F12FN410 Beacon 2 | Off | On |  |  |  | Activate bit when F12-FN-410 is Not Running. Will electrically activate local beacon within ROM tunnel. | 2
|  |  |  | YY12234C | YA12234C | 2000-F12-PID-PR-10001 | F12-FN-410 Primary Crusher 2 Buried Vault Ventilation Fan CV401 Tunnel Entrance 2 Warning Beacon | F12FN410 Beacon 3 | Off | On |  |  |  | Activate bit when F12-FN-410 is Not Running. Will electrically activate local beacon within ROM tunnel. | 2
|  |  |  | HS12562 | HS12562STT | 2000-F12-PID-PR-10002 | F12-DC-401 Primary Crusher 2 Dust Collector Start/Stop | F12DC401 Start/Stop | Off | On |  |  |  |  | 2
|  |  |  | XY12520 | XC12520 | 2000-F12-PID-PR-10002 | F12-MG-401 Primary Crusher Tramp Magnet 1 Remote Select | F12MG401 Remote Select | Activated | N_Activated |  |  |  | 2 Second Delay after activating Remote Select to activating Remote Run. | 2
|  |  |  | XY12521 | XC12521 | 2000-F12-PID-PR-10002 | F12-MG-401 Primary Crusher Tramp Magnet 1 Remote Run | F12MG401 Remote Run | Activated | N_Activated |  |  |  | Must have XC12520 active to be able to activate remote run. | 2
|  |  |  | XY12568 | XC12568 | 2000-F12-PID-PR-10002 | F12-MG-402 Primary Crusher Tramp Magnet 2 Remote Select | F12MG402 Remote Select | Activated | N_Activated |  |  |  | 2 Second Delay after activating Remote Select to activating Remote Run. | 2
|  |  |  | XY12569 | XC12569 | 2000-F12-PID-PR-10002 | F12-MG-402 Primary Crusher Tramp Magnet 2 Remote Run | F12MG402 Remote Run | Activated | N_Activated |  |  |  | Must have XC12568 active to be able to activate remote run. | 2
|  |  |  | HS12268 | HS12268STT | 2000-F12-PID-PR-10003 | F12-CU-401 Primary Crusher 2 Chiller Start / Stop | F12CU401 Run | Stop | Start |  |  |  | Primary Crusher 2 Oil Chiller Start/Stop Command. See Drives sheet for futther information. This digital output is used in auto control logic to switch chiller F12-CU-401 on/off based on process switchpoints. | 2
|  |  |  | XY12103 | XC12103 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher 2 Spider Lube System Pump Remote Run | F12LU402 Remote Start | Off | On |  |  |  | Remote run F12-LU-402 (F12-PO-419) via DCS. See Drives for further information. | 2
|  |  |  | SVO12122 | SIO12122 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Oil Filter Differential Pressure Switch High Solenoid Open | F12LU401 Solenoid Open | Off | On |  |  |  | Part of Primary Crusher 2 package. Part of SV12122 (See OnOff Valves sheet) | 2
|  |  |  | SVC12122 | SIC12122 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Oil Filter Differential Pressure Switch High Solenoid Close | F12LU401 Solenoid Close | Off | On |  |  |  | Part of Primary Crusher 2 package. Part of SV12122 (See OnOff Valves sheet) | 2
|  |  |  | XY12226 | XC12226 | 2000-F12-PID-PR-10001 | F12-LU-441 Primary Crusher 2 Discharge Apron Feeder Autolube Grease System Remote Start Control Signal | F12LU441 Remote Start | Off | On |  |  |  |  | 2
|  |  |  | XC12268B | XC12268B | 2000-F12-PID-PR-10003 | F12-CU-401 Primary Crusher 2 Chiller Control Mode | F12CU401 Ctrl Mode | Off | On |  |  |  |  | 2
|  |  |  | XY12563 | XC12563 | 2000-F12-PID-PR-10002 | F12-DC-401 Primary Crusher 2 Dust Collector Manual Override | F12DC401 Override | Normal | Active |  |  |  |  | 2
|  |  |  | F12SW012OP | F12SW012_OP | 2000-F12-PID-PR-10001 | Primary Crushing 11kV Switchboard Remote Switching Panel Open Breaker | F12SwRoom Breaker Opened | Inactive | Opened |  |  |  |  | 2
|  |  |  | F12SW012CL | F12SW012_CL | 2000-F12-PID-PR-10001 | Primary Crushing 11kV Switchboard Remote Switching Panel Close Breaker | F12SwRoom Breaker Closed | Inactive | Closed |  |  |  |  | 2
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 36 | 36
Update PCT from IO list and contractor checks

## 3. Digital Input
KCGM GROWTH PROJECT
|  |  |  | PROCESS CONTROL TABLES - CRUSHING |  |  |  |  | *SOFTWARE DEBOUNCE IS REQUIRED ON ALL DIGITAL INSTRUMENTS (NO HARDWARE DEBOUNCE)*
2000-F12-LST-PR-10001
DIGITAL INSTRUMENTS (DI)
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | P&ID | Description | Abbreviated Description (Faceplate) | State 0 | State 1 | Alarm State | Source | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev
|  |  |  | F12FIP001ALM | F12FIP001_ALM | 2000-F12-PID-PR-10001 | Primary Crushing 11kV / 415V Switchroom Fire Indicator Panel Alarm | F12SwRoom Fire Alarm | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 1
|  |  |  | F12FIP001FLT | F12FIP001_FLT | 2000-F12-PID-PR-10001 | Primary Crushing 11kV / 415V Switchroom Fire Indicator Panel Fault | F12SwRoom Fire Fault | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 1
|  |  |  | F12DCS401PS1 | F12DCS401_PS1 | 2000-F12-PID-PR-10001 | Primary Crushing 415V Switchroom DCS Panel Power Supply Healthy | F12 DCS Pwr Healthy | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 1
|  |  |  | F12UPS002ALMS | F12UPS002ALM | 2000-F12-PID-PR-10001 | Primary Crushing 415V Switchroom 240VAC UPS Alarm | F12SwRm 240VAC UPS Alarm | Alarm | Normal | Alarm | Soft Tag | 0 |  | Signal over modbus. | 2
|  |  |  | F12SW12SOP01S | F12SW012SOP01 | 2000-F12-PID-PR-10001 | Primary Crushing 11kV Switchboard Panel 1 Isolator Opened | F12SwBrd P1 Iso Open | N_Activated | Activated | Alarm | Soft Tag | 0 |  | Signal over modbus. | 2
|  |  |  | F12SW12SCL01S | F12SW012SCL01 | 2000-F12-PID-PR-10001 | Primary Crushing 11kV Switchboard Panel 1 Isolator Closed | F12SwBrd P1 Iso Clsd | N_Activated | Activated | Alarm | Soft Tag | 0 |  | Signal over modbus. | 2
|  |  |  | F12SW12SFH01S | F12SW012SFH01 | 2000-F12-PID-PR-10001 | Primary Crushing 11kV Switchboard Panel 1 Fuse Healthy | F12SwBrd P1 Fuse Healthy | Alarm | Normal | Alarm | Soft Tag | 0 |  | Signal over modbus. | 2
|  |  |  | F12SW12SOP02S | F12SW012SOP02 | 2000-F12-PID-PR-10001 | Primary Crushing 11kV Switchboard Panel 2 Circuit Breaker Opened | F12SwBrd P2 Breaker Open | N_Activated | Activated | Alarm | Soft Tag | 0 |  | Signal over modbus from F12SW012A02-R01 | 2
|  |  |  | F12SW12SCL02S | F12SW012SCL02 | 2000-F12-PID-PR-10001 | Primary Crushing 11kV Switchboard Panel 2 Circuit Breaker Closed | F12SwBrd P2 Breaker Clsd | N_Activated | Activated | Alarm | Soft Tag | 0 |  | Signal over modbus from F12SW012A02-R01 | 2
|  |  |  | F12SW12STR02S | F12SW012STR02 | 2000-F12-PID-PR-10001 | Primary Crushing 11kV Switchboard Panel 2 Circuit Breaker Tripped | F12SwBrd P2 Breaker Trip | Alarm | Normal | Alarm | Soft Tag | 0 |  | Signal over modbus from F12SW012A02-R01 | 2
|  |  |  | F12SW12SOP03S | F12SW012SOP03 | 2000-F12-PID-PR-10001 | Primary Crushing 11kV Switchboard Panel 3 Contactor Opened | F12SwBrd P3 Cont Open | N_Activated | Activated | Alarm | Soft Tag | 0 |  | Signal over modbus from F12SW012A03-R01 | 2
|  |  |  | F12SW12SCL03S | F12SW012SCL03 | 2000-F12-PID-PR-10001 | Primary Crushing 11kV Switchboard Panel 3 Contactor Closed | F12SwBrd P3 Cont Clsd | N_Activated | Activated | Alarm | Soft Tag | 0 |  | Signal over modbus from F12SW012A03-R01 | 2
|  |  |  | F12SW12SFH03S | F12SW012SFH03 | 2000-F12-PID-PR-10001 | Primary Crushing 11kV Switchboard Panel 3 Fuse Healthy | F12SwBrd P3 Fuse Healthy | Alarm | Normal | Alarm | Soft Tag | 0 |  | Signal over modbus from F12SW012A03-R01 | 2
|  |  |  | F12SW12SOP04S | F12SW012SOP04 | 2000-F12-PID-PR-10001 | Primary Crushing 11kV Switchboard Panel 4 Circuit Breaker Opened | F12SwBrd P4 Breaker Open | N_Activated | Activated | Alarm | Soft Tag | 0 |  | Signal over modbus from F12SW012A04-R01 | 2
|  |  |  | F12SW12SCL04S | F12SW012SCL04 | 2000-F12-PID-PR-10001 | Primary Crushing 11kV Switchboard Panel 4 Circuit Breaker Closed | F12SwBrd P4 Breaker Clsd | N_Activated | Activated | Alarm | Soft Tag | 0 |  | Signal over modbus from F12SW012A04-R01 | 2
|  |  |  | F12SW12STR04S | F12SW012STR04 | 2000-F12-PID-PR-10001 | Primary Crushing 11kV Switchboard Panel 4 Circuit Breaker Tripped | F12SwBrd P4 Breaker Trip | Alarm | Normal | Alarm | Soft Tag | 0 |  | Signal over modbus from F12SW012A04-R01 | 2
|  |  |  | F12SW12SOP05S | F12SW012SOP05 | 2000-F12-PID-PR-10001 | Primary Crushing 11kV Switchboard Panel 5 Circuit Breaker Opened | F12SwBrd P5 Breaker Open | N_Activated | Activated | Alarm | Soft Tag | 0 |  | Signal over modbus from F12SW012A05-R01 (Spare) | 2
|  |  |  | F12SW12SCL05S | F12SW012SCL05 | 2000-F12-PID-PR-10001 | Primary Crushing 11kV Switchboard Panel 5 Circuit Breaker Closed | F12SwBrd P5 Breaker Clsd | N_Activated | Activated | Alarm | Soft Tag | 0 |  | Signal over modbus from F12SW012A05-R01 (Spare) | 2
|  |  |  | F12SW12STR05S | F12SW012STR05 | 2000-F12-PID-PR-10001 | Primary Crushing 11kV Switchboard Panel 5 Circuit Breaker Tripped | F12SwBrd P5 Breaker Trip | Alarm | Normal | Alarm | Soft Tag | 0 |  | Signal over modbus from F12SW012A05-R01 (Spare) | 2
|  |  |  | F12SR001ESTP | F12SR001_ESTP | 2000-F12-PID-PR-10001 | Primary Crushing 11kV / 415V Switchroom Emergency Shutdown Healthy | F12SwRm Emerg Shut Hlthy | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 1
|  |  |  | F12DCS401PS2 | F12DCS401_PS2 | 2000-F12-PID-PR-10001 | Primary Crushing 415V Switchroom DCS Panel Power Supply Healthy | F12 DCS Pwr Healthy | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 1
|  |  |  | F12FIP001ISL | F12FIP001_ISL | 2000-F12-PID-PR-10001 | F12-FIP-001 Isolated | F12SwRoom Isolate | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 1
|  |  |  | F12RIO001PS1 | F12RIO001_PS1 | 2000-F12-PID-PR-10001 | F12-RIO-001 PS1 24VDC HEALTHY | F12RIO1 P1 Healthy | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 1
|  |  |  | F12RIO001PS2 | F12RIO001_PS2 | 2000-F12-PID-PR-10001 | F12-RIO-001 PS2 24VDC HEALTHY | F12RIO1 P2 Healthy | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 1
|  |  |  | F12RIO002PS1 | F12RIO002_PS1 | 2000-F12-PID-PR-10001 | F12-RIO-002 PS1 24VDC HEALTHY | F12RIO2 P1 Healthy | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 1
|  |  |  | F12RIO002PS2 | F12RIO002_PS2 | 2000-F12-PID-PR-10001 | F12-RIO-002 PS2 24VDC HEALTHY | F12RIO2 P2 Healthy | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 1
|  |  |  | F12SW101Q1CL | F12SW101_Q1CL | 2000-F12-PID-PR-10001 | F12-SW-101 Mains Supply CB Closed | F12SW101 Mains CB Closed | N_Activated | Activated | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | F12SW101Q1TRP | F12SW101_Q1OP | 2000-F12-PID-PR-10001 | F12-SW-101 Mains Supply CB Tripped | F12SW101 Mains CB Trip | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | F12SW101Q2CL | F12SW101_Q2CL | 2000-F12-PID-PR-10001 | F12-SW-101 Generator Supply CB Closed | F12SW101 Gen CB Closed | N_Activated | Activated | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | F12SW101Q2TRP | F12SW101_Q2OP | 2000-F12-PID-PR-10001 | F12-SW-101 Generator Supply CB Tripped | F12SW101 Gen CB Trip | Activated | N_Activated | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | F12SW012ESCL | F12SW012_ESCL | N/A | F12-SW-012 Earth Switch Closed | F12SW012 ES Closed | N_Activated | Activated |  | Hardwired to PCS |  |  |  | 2
|  |  |  | F12SW012ESOP | F12SW012_ESOP | N/A | F12-SW-012 Earth Switch Opened | F12SW012 ES Opened | N_Activated | Activated |  | Hardwired to PCS |  |  |  | 2
|  |  |  | PDSH12088 | PDAH12088 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Hydraulic System Oil Filter Differential Pressure Switch High | F12LU401 HydFilterDiffHi | Alarm | Normal | Alarm | Hardwired to PCS | 3 |  | As per FLS I/O List 2000-ME001.1-F17-50001 | 2
|  |  |  | PDSHH12088 | PDAHH12088 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Hydraulic System Oil Filter Differential Pressure Switch High High | F12LU401 HydFilterDiffHH | Alarm | Normal | Alarm | Hardwired to PCS | 3 |  | As per FLS I/O List 2000-ME001.1-F17-50001 | 2
|  |  |  | LSL12081 | LAL12081 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Hydraulic Oil Reservoir Level Switch | F12LU401 HydOilResvrLo | Closed (Low) | Normal | Closed (Low) | Hardwired to PCS | 3 |  | As per 2000-ME001.1-E03-50001 Setpoint as per FLS I/O List 2000-ME001.1-F17-50001 • Set switch to close at 66% of effective volume height (700mm * 0.66 = 462mm) | 2
|  |  |  | LSLL12081 | LALL12081 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Hydraulic Oil Reservoir Level Switch | F12LU401 HydOilResvrLL | Closed (Low Low) | Normal | Closed (Low Low) | Hardwired to PCS | 3 |  | As per 2000-ME001.1-E03-50001 Setpoint as per FLS I/O List 2000-ME001.1-F17-50001 • Set switch to close at 33% of effective volume height (700mm * 0.33 = 231mm,) | 2
|  |  | X | XS12100 | XA12100 | 2000-F12-PID-PR-10001 | F12-LU-402 Primary Crusher 2 Spider Lubrication System End Cycle Position Switch | F12LU402 Cycle End Sw | Activated | Normal |  | Hardwired to PCS |  |  | Please see F12-LU-402_T1 for further details in 12. Misc sheet. Switch activates at end of cycle. For further details, please refer to 2000-ME001.1-F17-50001. | 2
|  |  |  | HS12101 | HS12101STT | 2000-F12-PID-PR-10001 | F12-LU-402 Primary Crusher 2 Spider Lubrication Sytem Start Push Button LCP | F12LU402 Start | Normal | Activated |  | Hardwired to PCS |  |  | Push button on LCP. When activated AND F12LU402 in LOCAL, HS12101 to start system (F12-PO-419). | 2
|  |  |  | XS12104 | XI12104 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher 2 Spider Lube System Pump Ready | F12LU402 Spider Ready | N_Ready | Ready |  | Hardwired to PCS |  |  |  | 2
|  |  |  | XS12105 | XI12105 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher 2 Spider Lube System Pump Running | F12LU402 Spider Running | N_Running | Running |  | Hardwired to PCS |  |  |  | 2
|  |  |  | LSL12111 | LAL12111 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Lube Oil Reservoir Level Switch | F12LU401 LubeOilResvrLo | Closed (Low) | Normal | Closed (Low) | Hardwired to PCS | 3 |  | As per 2000-ME001.1-E03-50001. Setpoint as per FLS I/O List 2000-ME001.1-F17-50001 • Set switch to close at 66% of effective volume height. | 2
|  |  |  | LSLL12111 | LALL12111 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Lube Oil Reservoir Level Switch | F12LU401 LubeOilResvrLL | Closed (Low Low) | Normal | Closed (Low Low) | Hardwired to PCS | 3 |  | As per 2000-ME001.1-E03-50001. Setpoint as per FLS I/O List 2000-ME001.1-F17-50001 • Set switch to close at 33% of effective volume height. | 2
|  |  |  | PDSH12121 | PDAH12121 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Oil Filter Differential Pressure Switch High | F12LU401 LubeFlterDiffHi | Alarm | Normal | Alarm | Hardwired to PCS | 3 |  | As per FLS I/O List 2000-ME001.1-F17-50001. | 2
|  | Update PCT from IO list and contractor checks |  | PDSHH12121 | PDAHH12121 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Oil Filter Differential Pressure Switch High High | F12LU401 LubeFlterDiffHH | Alarm | Normal | Alarm | Hardwired to PCS | 3 |  | As per FLS I/O List 2000-ME001.1-F17-50001. | 2
|  |  |  | LSH12201 | LAH12201 | 2000-F12-PID-PR-10001 | F12-BN-405 Primary Crusher 2 Surge Bin Primary Crusher 2 Surge Bin Level Switch High | F12BN405 Prim. Cr 2 LAH | Alarm | Normal | Alarm | Hardwired to PCS | 3 |  |  | 2
|  |  |  | LSH12227 | LAH12227 | 2000-F12-PID-PR-10001 | F12-CH-402 Primary Crusher Discharge Apron Feeder Head Chute Blocked Chute Receive | F12CH402 Blocked Chute | Alarm | Normal | Alarm | Hardwired to PCS | 3 |  |  | 2
|  |  |  | LSH12370 | LAH12370 | 2000-F12-PID-PR-10001 | F12-PS-401 Primary Crusher 2 Area Sump Pump Level Switch High | F12PS401 Crusher Sump | Normal | Alarm | Alarm | Soft Tag | 3 |  | Wired directly to the motor starter | 2
|  |  |  | ZE12222 | SAL12222 | 2000-F12-PID-PR-10001 | F12-FA-401 Primary Crusher 2 Discharge Apron Feeder Position Encoder | F12FA401 Underspeed | Alarm | Normal | Alarm | Soft Tag | 0 | F12-FA-401 Not Running | Set at less than or equal <= 2 RPM. Alarm enabled delay of 10 seconds on Feeder F12-FA-401 start-up. Source: 2000-ME004-M01-10001 Wired directly to the motor starter | 2
|  |  |  | PWS12221A | PWA12221A | 2000-F12-PID-PR-10001 | F12-FA-401 Primary Crusher 2 Discharge Apron Feeder Pull-Wire Switch RHS | F12FA401 P/W RHS | Activated | Normal | Activated | Hardwired to PCS | 0 |  |  | 0
|  |  |  | PWS12221B | PWA12221B | 2000-F12-PID-PR-10001 | F12-FA-401 Primary Crusher 2 Discharge Apron Feeder Pull-Wire Switch LHS | F12FA401 P/W LHS | Activated | Normal | Activated | Hardwired to PCS | 0 |  |  | 0
|  |  |  | TS12237 | TSH12237 | 2000-F12-PID-PR-10001 | F12-FA-401 Primary Crusher 2 Discharge Apron Feeder Gearbox Fan Cooler Temperature Switch | F12FA401 Gearbox Fan Sw | Activated | Normal |  | Hardwired to PCS | 3 |  | Apron Feeder Cooler Temperature Switch. When activated, air-oil cooler fan will switch on (at temperatures greater than 50C). Fan will switch off when temperature is < 35C. Source: 2000-ME004-M01-10001. | 2
|  |  |  | PDSH12230 | PDAH12230 | 2000-F12-PID-PR-10001 | F12-PO-436 Primary Crusher 2 Discharge Apron Feeder Gearbox Cooler Oil Pump Filter Pressure Differential Switch High | F12PO436 Filter Delta | Activated | Normal | Activated | Hardwired to PCS | 3 | Mask if F12-PO-436 Not Running | Gearbox Cooler Filter Clogging Indicator. Differential pressure is above 1.5 bar. Alarm if PDAH12230 Active. | 2
|  |  |  | PS12231 | PAL12231 | 2000-F12-PID-PR-10001 | F12-PO-436 Primary Crusher 2 Discharge Apron Feeder Gearbox Cooler Oil Pump Pressure Switch | F12PO436 G/Box | Activated | Normal | Activated | Hardwired to PCS | 3 | Mask if F12-PO-436 Not Running | Gearbox Oil Cooler Pressure Switch. Oil pump fault. Discharge pressure < 0.7 bar. Alarm enabled delay on F12PO436 startup of 15 seconds. | 2
|  |  |  | SSL12510 | SAL12510 | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Tail End Speed Sensor | F12CV401 Under Speed | Alarm | Normal | Alarm | Hardwired to PCS | 3 | F12-CV-401 Not Running and Mask on start-up |  | 2
|  |  |  | PWS12501A | PWA12501A | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Tail End Pull-Wire Switch 1 RHS | F12CV401 Tail P/W RHS | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | PWS12501B | PWA12501B | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Tail End Pull-Wire Switch 1 LHS | F12CV401 Tail P/W LHS | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | BRS12504 | BRA12504 | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Loading Chute Belt Rip Switch | F12CV401 Belt Rip | Alarm | Normal | Alarm | Hardwired to PCS | 3 |  |  | 2
|  |  |  | PWS12501C | PWA12501C | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Head End Pull-Wire Switch 2 RHS | F12CV401 Head P/W RHS | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | PWS12501D | PWA12501D | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Head End Pull-Wire Switch 2 LHS | F12CV401 Head P/W LHS | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | ZS12506A | ZSA12506A | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Take-Up Upper Limit Limit Switch | F12CV401 Take-Up LHS | Alarm | Normal | Alarm | Hardwired to PCS | 3 | F12-CV-401 Not Running |  | 2
|  |  |  | ZS12506B | ZSA12506B | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Take-Up Lower Limit Limit Switch | F12CV401 Take-Up RHS | Alarm | Normal | Alarm | Hardwired to PCS | 3 | F12-CV-401 Not Running |  | 2
|  |  |  | ZE12502 | SAL12502 | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Drive Pulley Speed Encoder | F12CV401 H/E Belt Speed | Alarm | Normal | Alarm | Soft Tag | 3 | F12-CV-401 Not Running and Mask on start-up | Wired directly to the motor starter. | 2
|  |  |  | LSH12511 | LAH12511 | 2000-F12-PID-PR-10002 | F12-CH-405 Primary Crusher DIscharge Conveyor Head Chute Blocked Chute Receive | F12CV401 Blocked Chute | Alarm | Normal | Alarm | Hardwired to PCS | 3 |  |  | 2
|  |  |  | BDS12503A | BDA12503A | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Loading Chute Belt Drift Switch RHS | F12CV401 Tail Drift RHS | Alarm | Normal | Alarm | Hardwired to PCS | 3 | F12-CV-401 Not Running |  | 2
|  |  |  | BDS12503B | BDA12503B | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Loading Chute Belt Drift Switch LHS | F12CV401 Tail Drift LHS | Alarm | Normal | Alarm | Hardwired to PCS | 3 | F12-CV-401 Not Running |  | 2
|  |  |  | BDS12503C | BDA12503C | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Head End Belt Drift Switch RHS | F12CV401 Head Drift RHS | Alarm | Normal | Alarm | Hardwired to PCS | 3 | F12-CV-401 Not Running |  | 2
|  |  |  | BDS12503D | BDA12503D | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Head End Belt Drift Switch LHS | F12CV401 Head Drift LHS | Alarm | Normal | Alarm | Hardwired to PCS | 3 | F12-CV-401 Not Running |  | 2
|  |  |  | BDS12503E | BDA12503E | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Take Up Return Belt Drift Switch RHS | F12CV401 TakeUpDrift RHS | Alarm | Normal | Alarm | Hardwired to PCS | 3 | F12-CV-401 Not Running |  | 2
|  |  |  | BDS12503F | BDA12503F | 2000-F12-PID-PR-10002 | F12-CV-401 Primary Crusher Discharge Conveyor Take Up Return Belt Drift Switch LHS | F12CV401 TakeUpDrift LHS | Alarm | Normal | Alarm | Hardwired to PCS | 3 | F12-CV-401 Not Running |  | 2
|  |  |  | XS12519 | XA12519 | 2000-F12-PID-PR-10002 | F12-MG-401 Primary Crusher Tramp Magnet 1 System Fault | F12MG401 System Fault | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | XS12518 | XI12518 | 2000-F12-PID-PR-10002 | F12-MG-401 Primary Crusher Tramp Magnet 1 System Running | F12MG401 System Running | N_Running | Running |  | Hardwired to PCS | 0 |  |  | 2
|  |  |  | XS12517 | XI12517 | 2000-F12-PID-PR-10002 | F12-MG-401 Primary Crusher Tramp Magnet 1 System Ready | F12MG401 System Ready | N_Ready | Ready |  | Hardwired to PCS | 0 |  |  | 2
|  |  |  | XA12563 | XA12563 | 2000-F12-PID-PR-10002 | Primary Crusher 2 Dust Collector System Fault | F12DC401 System Fault | Alarm | Normal | Alarm | Hardwired to PCS | 3 |  |  | 2
|  |  |  | XI12564 | XI12564 | 2000-F12-PID-PR-10002 | Primary Crusher 2 Dust Collector System Running | F12DC401 System Running | N_Running | Running |  | Hardwired to PCS | 3 |  |  | 2
|  |  |  | SSL12553 | SAL12553 | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Tail End Underspeed Switch | F12CV402 Tail Underspeed | Alarm | Normal | Alarm | Hardwired to PCS | 3 | F12-CV-402 Not Running and Mask on start-up |  | 2
|  |  |  | BRS12556 | BRA12556 | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Loading Chute Belt Rip Switch | F12CV402 Belt Rip Switch | Alarm | Normal | Alarm | Hardwired to PCS | 3 |  |  | 2
|  |  |  | BDS12555A | BDA12555A | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Tail End Return Belt Drift Switch RHS | F12CV402 Tail Drift RHS | Alarm | Normal | Alarm | Hardwired to PCS | 3 | F12-CV-402 Not Running |  | 2
|  |  |  | BDS12555B | BDA12555B | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Tail End Return Belt Drift Switch LHS | F12CV402 Tail Drift LHS | Alarm | Normal | Alarm | Hardwired to PCS | 3 | F12-CV-402 Not Running |  | 2
|  |  |  | PWS12552A | PWA12552A | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Tail End Pull-Wire Switch 1 RHS | F12CV402 Tail P/W RHS | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | PWS12552B | PWA12552B | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Tail End Pull-Wire Switch 1 LHS | F12CV402 Tail P/W LHS | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | PWS12552C | PWA12552C | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Head End Pull-Wire Switch 2 RHS | F12CV402 Mid P/W (RHS) | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | PWS12552D | PWA12552D | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Head End Pull-Wire Switch 2 LHS | F12CV402 Mid P/W LHS | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | ZS12558A | ZSA12558A | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Take-Up Upper Limit Limit Switch | F12CV402 Takeup Left | Alarm | Normal | Alarm | Hardwired to PCS | 3 | F12-CV-402 Not Running |  | 2
|  |  |  | ZS12558B | ZSA12558B | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Take-Up Lower Limit Limit Switch | F12CV402 Takeup Right | Alarm | Normal | Alarm | Hardwired to PCS | 3 | F12-CV-402 Not Running |  | 2
|  |  |  | YE12523 | YI12523 | 2000-F12-PID-PR-10002 | F12-AN-407 Coarse Ore Stockpile Feed Particle Size Analyser Output | F12AN407 Output | N_Activated | Activated |  | Soft Tag | 0 |  | Coarse Ore Stockpile Feed Particle Size Analyser. Input Tag: vision/camera-name/p80 Please see: 2000-SPC-CS-110001 for details. | 2
|  |  |  | ZE12554 | SAL12554 | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Drive Pulley Speed Encoder | F12CV402 Pulley U/Speed | Alarm | Normal | Alarm | Soft Tag | 0 | F12-CV-402 Not Running and Mask on start-up | Wired directly to the motor starter. | 2
|  |  |  | BDS12555C | BDA12555C | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Head End Belt Drift Switch RHS | F12CV402 Head Drift RHS | Alarm | Normal | Alarm | Hardwired to PCS | 3 | F12-CV-402 Not Running |  | 2
|  |  |  | BDS12555D | BDA12555D | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Head End Belt Drift Switch LHS | F12CV402 Head Drift LHS | Alarm | Normal | Alarm | Hardwired to PCS | 3 | F12-CV-402 Not Running |  | 2
|  |  |  | BDS12555E | BDA12555E | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Take Up Return Belt Drift Switch RHS | F12CV402 TakeUpDrift RHS | Alarm | Normal | Alarm | Hardwired to PCS | 3 | F12-CV-402 Not Running |  | 2
|  |  |  | BDS12555F | BDA12555F | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Take Up Return Belt Drift Switch LHS | F12CV402 TakeUpDrift LHS | Alarm | Normal | Alarm | Hardwired to PCS | 3 | F12-CV-402 Not Running |  | 2
|  |  |  | BDS12555G | BDA12555G | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Loading Chute Belt Drift Switch RHS | F12CV402 Chute Drift RHS | Alarm | Normal | Alarm | Hardwired to PCS | 3 | F12-CV-402 Not Running |  | 2
|  |  |  | BDS12555H | BDA12555H | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Loading Chute Belt Drift Switch LHS | F12CV402 Chute Drift LHS | Alarm | Normal | Alarm | Hardwired to PCS | 3 | F12-CV-402 Not Running |  | 2
|  |  |  | LSH12582 | LAH12582 | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Blocked Chute Receive | F12CV402 Blocked Chute | Alarm | Normal | Alarm | Hardwired to PCS | 3 |  |  | 2
|  |  |  | XS12567 | XA12567 | 2000-F12-PID-PR-10002 | F12-MG-402 Primary Crusher Tramp Magnet 2 System Fault | F12MG402 System Fault | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | XS12566 | XI12566 | 2000-F12-PID-PR-10002 | F12-MG-402 Primary Crusher Tramp Magnet 2 System Running | F12MG402 System Running | N_Running | Running |  | Hardwired to PCS | 0 |  |  | 2
|  |  |  | XS12565 | XI12565 | 2000-F12-PID-PR-10002 | F12-MG-402 Primary Crusher Tramp Magnet 2 System Ready | F12MG402 System Ready | N_Ready | Ready |  | Hardwired to PCS | 0 |  |  | 2
|  |  |  | LSL12225 | LAL12225 | 2000-F12-PID-PR-10001 | F12-LU-441 Primary Crusher 2 Discharge Apron Feeder Autolube Grease System Lube Level Switch Low | F12FA401 Grease Level | Activated | N_Activated | Activated | Hardwired to PCS | 3 |  | Apron Feeder Grease System Level Low | 2
|  |  |  | XS12224 | XA12224 | 2000-F12-PID-PR-10001 | F12-LU-441 Primary Crusher 2 Discharge Apron Feeder Autolube Grease System End Cycle Position Switch | F12FA401 Grease Cycle Sw | N_Activated | Activated | N_Activated | Hardwired to PCS | 10 | Mask if F12-LU-441 Not Running | Switch to pulse when Grease Pump (F12-LU-441) is running. Alarm if F12-LU-441 Running AND XA12224 Not Active. Refer to 2000-ME004-M01-10001 for further details. | 2
|  |  |  | LSHH13001 | LAHH13001 | 2000-F13-PID-PR-10001 | F12-SKP-401 Coarse Ore Stockpile 2 Level Switch High High | F12SKP401 Stockpile 2 | Alarm | Normal | Alarm | Hardwired to PCS | 3 |  | Blocked chute switch. When activated, trip F12-CV-402. | 2
|  |  |  | AS12125 | AAH12125 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Oil Return Moisture Analyser Switch | F12LU401 Return Moisture | Alarm | Normal | Alarm | Hardwired to PCS | 3 |  | Setpoint as per FLS I/O List 2000-ME001.1-F17-50001 • Activate alarm at 80% Relative Humidity. | 2
|  |  |  | FS12145 | FAL12145 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Heat Exchanger Cooling Water Return Flow Switch | F12LU401 HX Cool Water | Open | Closed | Open | Hardwired to PCS | 10 | Duty F12PW425/426 Not Running | Switch to be configured such that it closes with increasing flow. When no-flow detected (switch is open) alarm, mask if F12-PW-425 AND 426 is not running. | 2
|  |  |  | HS12130 | HS12130ESTP | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Control Panel Emergency Stop | F12LU401 EStop Active | Alarm | Normal | Alarm | Soft Tag | 0 |  | Lubrication and Hydraulic System Junction Box E-Stop. Source: 2000-ME001.1-F17-50001. Wired directly to the motor starter. | 2
|  |  |  | HS12131A | HS12131ASTT | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Control Panel Hydraulic Pump 1 Start Push Button | F12PO403 Start Local | N_Activated | Activated |  | Hardwired to PCS | 0 |  | Hand switch can only be used in LOCAL mode. HS to start pump. If Activated, DCS Prompt to switch pump to local. | 2
|  |  |  | HS12132A | HS12132ASTT | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Control Panel Hydraulic Pump 2 Start Push Button | F12PO410 Start Local | N_Activated | Activated |  | Hardwired to PCS | 0 |  | Hand switch can only be used in LOCAL mode. HS to start pump. If Activated, DCS Prompt to switch pump to local. | 2
|  |  |  | HS12133A | HS12133ASTT | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Control Panel Lubrication Pump 1 Start Push Button | F12PO404 Start Local | N_Activated | Activated |  | Hardwired to PCS | 0 |  | Hand switch can only be used in LOCAL mode. HS to start pump. If Activated, DCS Prompt to switch pump to local. | 2
|  |  |  | HS12134A | HS12134ASTT | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Control Panel Lubrication Pump 2 Start Push Button | F12PO405 Start Local | N_Activated | Activated |  | Hardwired to PCS | 0 |  | Hand switch can only be used in LOCAL mode. HS to start pump. If Activated, DCS Prompt to switch pump to local. | 2
|  |  |  | HS12131B | HS12131BSTP | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Control Panel Hydraulic Pump 1 Stop Push Button | F12PO403 Stop Local | N_Activated | Activated |  | Hardwired to PCS | 0 |  | Hand switch can only be used in LOCAL mode. HS to stop pump. If Activated, DCS Prompt to switch pump to local. | 2
|  |  |  | HS12132B | HS12132BSTP | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Control Panel Hydraulic Pump 2 Stop Push Button | F12PO410 Stop Local | N_Activated | Activated |  | Hardwired to PCS | 0 |  | Hand switch can only be used in LOCAL mode. HS to stop pump. If Activated, DCS Prompt to switch pump to local. | 2
|  |  |  | HS12133B | HS12133BSTP | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Control Panel Lubrication Pump 1 Stop Push Button | F12PO404 Stop Local | N_Activated | Activated |  | Hardwired to PCS | 0 |  | Hand switch can only be used in LOCAL mode. HS to stop pump. If Activated, DCS Prompt to switch pump to local. | 2
|  |  |  | HS12134B | HS12134BSTP | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Control Panel Lubrication Pump 2 Stop Push Button | F12PO405 Stop Local | N_Activated | Activated |  | Hardwired to PCS | 0 |  | Hand switch can only be used in LOCAL mode. HS to stop pump. If Activated, DCS Prompt to switch pump to local. | 2
|  |  |  | ZSO12122 | ZIO12122 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Heat Exchanger Drain Valve Position Switch Opened | XV12122 Lube Drain Open | Open | N_Open |  | Hardwired to PCS | 0 |  | Part of Primary Crusher 2 package. Part of SV12122 (See OnOff Valves sheet) | 2
|  |  |  | ZSC12122 | ZIC12122 | 2000-F12-PID-PR-10001 | F12-LU-401 Primary Crusher 2 Lubrication System Heat Exchanger Drain Valve Position Switch Closed | XV12122 Lube Drain Clsd | Closed | N_Closed |  | Hardwired to PCS | 0 |  | Part of Primary Crusher 2 package. Part of SV12122 (See OnOff Valves sheet) | 2
|  |  | X | HS12062 | HS12062UP | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher 2 Mantle Raise Push Button | F12CG401 Mantle Raise | N_Active | Activated |  | Hardwired to PCS | 0 |  | Physical button to have effect if F12-CG-401 is in LOCAL mode. If not in Local and button depressed: DCS Prompt to approve mantle raise. On approval F12-SEQ-0006 to initiate. Please create a DCS graphic button for the Control Room Operator to push with left-click mouse button to remotely adjust mantle position. This may be completed when Crusher is in MANUAL OR AUTO. Please see F12-SEQ-0006 and the 8. PID Cont tab for further details. ZIC12062 P_Lo interlock applies. | 2
|  |  | X | HS12063 | HS12063DN | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher 2 Mantle Lower Push Button | F12CG401 Mantle Lower | N_Active | Activated |  | Hardwired to PCS | 0 |  | Physical button to have effect if F12-CG-401 is in LOCAL mode. If not in Local and button depressed: DCS Prompt to approve mantle raise. On approval F12-SEQ-0007 to initiate. Please create a DCS graphic button for the Control Room Operator to push with left-click mouse button to remotely adjust mantle position. This may be completed when Crusher is in MANUAL OR AUTO. Please see F12-SEQ-0007 and the 8. PID Cont tab for further details. ZIC12062 P_Hi interlock applies. | 2
|  |  |  | HS12019A | HS12019AEN | 2000-F12-PID-PR-10001 | F12-RB-401 Rock Breaker Run Enable | F12RB401 Run Enable | Normal | Activated |  | Soft Tag | 0 |  | When activated, prompt to appear in DCS: "Approve use of Rock Breaker, note Primary Crusher 2 will interlock to stop << YES >> << CANCEL >>". See Misc sheet for further details. | 2
|  |  |  | PDSH12019B | PDAH12019B | 2000-F12-PID-PR-10001 | F12-RB-401 Rock Breaker HPU Blocked Filter Pressure Differential Switch Active | F12RB401 HPU Flilter | Normal | Activated | Activated | Soft Tag | 3 |  | TBC Vendor Details. | 2
|  |  |  | XI12019CS | XI12019C | 2000-F12-PID-PR-10001 | F12-RB-401 Rock Breaker Maintenance Position | F12RB401 Maintenance | Maint | N_Maint |  | Soft Tag | 0 |  | TBC Vendor Details. | 2
|  |  |  | XI12019DS | XI12019D | 2000-F12-PID-PR-10001 | F12-RB-401 Rock Breaker Home Position | F12RB401 Home | Home | N_Home |  | Soft Tag | 0 |  | TBC Vendor Details. | 2
|  |  |  | XI12019ES | XI12019E | 2000-F12-PID-PR-10001 | F12-RB-401 Rock Breaker System Ready | F12RB401 Breaker Ready | N_Ready | Ready |  | Soft Tag | 0 |  | TBC Vendor Details. | 2
|  |  |  | XI12019FS | XI12019F | 2000-F12-PID-PR-10001 | F12-RB-401 Rock Breaker System Running | F12RB401 Running | N_Running | Running |  | Soft Tag | 0 |  | TBC Vendor Details. | 2
|  |  |  | XI12019GS | XI12019G | 2000-F12-PID-PR-10001 | F12-RB-401 Rock Breaker General Fault | F12RB401 Breaker Fault | N_Activated | Activated | Activated | Soft Tag | 0 |  | TBC Vendor Details. | 2
|  |  |  | XS12268A | XA12268 | 2000-F12-PID-PR-10003 | F12-CU-401 Primary Crusher 2 Chiller Fault | F12CU401 Chiller Fault | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | XS12268B | XI12268A | 2000-F12-PID-PR-10003 | F12-CU-401 Primary Crusher 2 Chiller Running | F12CU401 Running | N_Running | Running |  | Hardwired to PCS | 0 |  |  | 2
|  |  |  | XS12268C | XI12268B | 2000-F12-PID-PR-10003 | F12-CU-401 Primary Crusher 2 Chiller Ready | F12CU401 Ready | N_Ready | Ready |  | Hardwired to PCS | 0 |  |  | 2
|  |  |  | F12SW001OP | F12SW001_OP | 2000-F12-PID-PR-10001 | Primary Crushing 415V MCC Circuit Breaker Opened | F12 MCC Breaker Opn | N_Activated | Activated | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | F12SW001CL | F12SW001_CL | 2000-F12-PID-PR-10001 | Primary Crushing 415V MCC Circuit Breaker Closed | F12 MCC Breaker Clsd | N_Activated | Activated | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | F12SW001TRP | F12SW001_TRP | 2000-F12-PID-PR-10001 | Primary Crushing 415V MCC Circuit Breaker Tripped | F12 MCC Breaker Trip | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | F12SW001SD | F12SW001_SD | 2000-F12-PID-PR-10001 | Primary Crushing 415V MCC Incomer Surge Diverter Healthy | F12 MCC Incomer Healthy | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | F12SW001AF | F12SW001_AF | 2000-F12-PID-PR-10001 | Primary Crushing 415V MCC Arc Flash protection System Power Healthy | F12 MCC ArcFlash Healthy | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | F12BC001FL3 | F12BC001_FL3 | 2000-F12-PID-PR-10001 | Primary Crushing 11kV Switchroom 48V Charger Alarm | F12SwRm 48V Charger | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | F12SW012SELS | F12SW012SEL | 2000-F12-PID-PR-10001 | Primary Crushing 11kV Switchboard Remote Switching Panel Remote Selected | F12SwBrd Remote Selected | Activated | Normal |  | Soft Tag | 0 |  | Signal over modbus. | 2
|  |  |  | F12SW001SELS | F12SW001SEL | 2000-F12-PID-PR-10001 | Primary Crushing 415V MCC Remote Switching Panel Remote Selected | F12MCC Remote Selected | Activated | Normal |  | Soft Tag | 0 |  | Signal over modbus. | 2
|  |  |  | SSL12545 | SAL12545 | 2000-F12-PID-PR-10002 | F12-DC-401 Primary Crusher 2 Dust Collector Rotary Valve Underspeed Switch | F12DC401 Rotary U/Speed | Alarm | Normal | Alarm | Hardwired to PCS | 3 | F12-VR-401 Not Running | Mask when F12-VR-401 Primary Crusher 2 Dust Rotary Valve is not running. Note: The input for this SSL is pulsing while rotary valve is running. Vendor discretion to come up with a pulse counter and appropriate alarm generation. | 2
|  |  |  | LSL12202 | LAL12202 | 2000-F12-PID-PR-10001 | F12-HU-401 Crushign Vault Lower Door HPU Reservoir Level Low Switch | F12HU401 Hydraulic Tank | Alarm | Normal | Alarm | Hardwired to PCS | 3 |  | When active, interlocks to F12-HU-401 . | 2
|  |  |  | ZSO12202 | ZIO12202 | 2000-F12-PID-PR-10001 | F12-HU-401 Vault Door Hydraulic Power Pack - Door 1 Hydraulic Cylinder 1 Valve Position Switch Opened | F12HU401 Door 1 | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | ZSC12202 | ZIC12202 | 2000-F12-PID-PR-10001 | F12-HU-401 Vault Door Hydraulic Power Pack - Door 1 Hydraulic Cylinder 1 Valve Position Switch Closed | F12HU401 Door 1 | Activated | Normal |  | Hardwired to PCS | 0 |  |  | 2
|  |  |  | ZS12300A | ZI12300A | 2000-F12-PID-PR-10001 | F12-CR-401 Primary Crusher Overhead Crane Position Switch | F12CR401 Position A | Activated | Normal |  | Hardwired to PCS | 0 |  |  | 2
|  |  |  | ZS12300B | ZI12300B | 2000-F12-PID-PR-10001 | F12-CR-401 Primary Crusher Overhead Crane Position Switch | F12CR401 Position B | Activated | Normal |  | Hardwired to PCS | 0 |  |  | 2
|  |  |  | ZS12301A | ZI12301A | 2000-F12-PID-PR-10001 | F12-LE-401 Primary Crusher Hydroset Trolley Position Switch | F12LE401 Hydroset Posn A | Activated | Normal |  | Hardwired to PCS | 0 |  |  | 2
|  |  |  | ZS12301B | ZI12301B | 2000-F12-PID-PR-10001 | F12-LE-401 Primary Crusher Hydroset Trolley Position Switch | F12LE401 Hydroset Posn B | Activated | Normal |  | Hardwired to PCS | 0 |  |  | 2
|  |  |  | FSLL12266 | FALL12266 | 2000-F12-PID-PR-10003 | F12-CU-401 Primary Crusher 2 Chiller Inlet Water Flow Switch Low Low | F12CU401 Inlet Water | Alarm | Normal | Alarm | Hardwired to PCS | 3 | Duty F12PW425/426 Not Running | On inlet of Primary Crusher 2 Chiller. | 2
|  |  |  | ZSO12262 | ZIO12262 | 2000-F12-PID-PR-10003 | F12-PW-425 Primary Crusher 2 Cooling Water Pump 1 Suction Valve Position Switch Open | F12PW425 Suction Valve | Open | N_Open |  | Hardwired to PCS | 0 |  | Manual valves with positioner feedback. | 2
|  |  |  | ZSC12262 | ZIC12262 | 2000-F12-PID-PR-10003 | F12-PW-425 Primary Crusher 2 Cooling Water Pump 1 Suction Valve Position Switch Closed | F12PW425 Suction Valve | Closed | N_Closed |  | Hardwired to PCS | 0 |  | Manual valves with positioner feedback. | 2
|  |  |  | ZSO12263 | ZIO12263 | 2000-F12-PID-PR-10003 | F12-PW-425 Primary Crusher 2 Cooling Water Pump 1 Discharge Valve Position Switch Open | F12PW425 Discharge Valve | Open | N_Open |  | Hardwired to PCS | 0 |  | Manual valves with positioner feedback. | 2
|  |  |  | ZSC12263 | ZIC12263 | 2000-F12-PID-PR-10003 | F12-PW-425 Primary Crusher 2 Cooling Water Pump 1 Discharge Valve Position Switch Closed | F12PW425 Discharge Valve | L | N_Closed |  | Hardwired to PCS | 0 |  | Manual valves with positioner feedback. | 2
|  |  |  | ZSO12264 | ZIO12264 | 2000-F12-PID-PR-10003 | F12-PW-426 Primary Crusher 2 Cooling Water Pump 2 Suction Valve Position Switch Open | F12PW426 Suction Valve | Open | N_Open |  | Hardwired to PCS | 0 |  | Manual valves with positioner feedback. | 2
|  |  |  | ZSC12264 | ZIC12264 | 2000-F12-PID-PR-10003 | F12-PW-426 Primary Crusher 2 Cooling Water Pump 2 Suction Valve Position Switch Closed | F12PW426 Suction Valve | Closed | N_Closed |  | Hardwired to PCS | 0 |  | Manual valves with positioner feedback. | 2
|  |  |  | ZSO12265 | ZIO12265 | 2000-F12-PID-PR-10003 | F12-PW-426 Primary Crusher 2 Cooling Water Pump 2 Discharge Valve Position Switch Open | F12PW426 Discharge Valve | Open | N_Open |  | Hardwired to PCS | 0 |  | Manual valves with positioner feedback. | 2
|  |  |  | ZSC12265 | ZIC12265 | 2000-F12-PID-PR-10003 | F12-PW-426 Primary Crusher 2 Cooling Water Pump 2 Discharge Valve Position Switch Closed | F12PW426 Discharge Valve | Closed | N_Closed |  | Hardwired to PCS | 0 |  | Manual valves with positioner feedback. | 2
|  |  |  | F12SW001PS | F12SW001_PS | 2000-F12-PID-PR-10002 | F12-SW-001 ACB SHUNT TRIP 24VDC OK | F12CB Shunt Trip | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | F12SW001PS1 | F12SW001_PS1 | 2000-F12-PID-PR-10001 | F12-SW-001 PS1 24VDC HEALTHY | F12SWR P1 Healthy | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | F12SW001PS2 | F12SW001_PS2 | 2000-F12-PID-PR-10001 | F12-SW-001 PS1 24VDC HEALTHY | F12SWR P2 Healthy | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | F12BC001FL1 | F12BC001_FL1 | 2000-F12-PID-PR-10001 | F12-BC-001 48VDC Charger Mains Fail | F12Mains Fail | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | F12BC001FL2 | F12BC001_FL2 | 2000-F12-PID-PR-10001 | F12-BC-001 48VDC Charger Battery Fail | F12Char Batt Fail | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | F12BC001FL4 | F12BC001_FL4 | 2000-F12-PID-PR-10001 | F12-BC-001 48VDC Charger Earth Fault | F12Char Earth Fault | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | WQS12557 | WS12557 | 2000-F12-PID-PR-10002 | F12-WD-402 STOCKPILE FEED CONVEYOR WEIGHTOMETER Pulse Tonnes | F12WD402 Weight Pulse | Off | On |  | Hardwired to PCS | 0 |  |  | 2
|  |  |  | XS12557 | XA12557 | 2000-F12-PID-PR-10002 | F12-WD-402 STOCKPILE FEED CONVEYOR WEIGHTOMETER Alarm | F12WD402 Weight Alarm | Normal | Alarm | Alarm | Hardwired to PCS | 3 |  |  | 2
|  |  |  | F12SW101SD | F12SW101_SD | 2000-F12-PID-PR-10001 | F12-SW-101 Surge Diverter Ok | F12SW101 Surge Diverter | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | LSHH12013 | LAHH12013 | 2000-F12-PID-PR-10001 | F12-GE-101 Primary Crushing Essential Supply 415V Generator Fuel Level Switch High High | F12GE101 Fuel Level | Normal | Alarm | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | LSH12013 | LAH12013 | 2000-F12-PID-PR-10001 | F12-GE-101 Primary Crushing Essential Supply 415V Generator Fuel Level Switch High | F12GE101 Fuel Level | Normal | Alarm | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | LSL12013 | LAL12013 | 2000-F12-PID-PR-10001 | F12-GE-101 Primary Crushing Essential Supply 415V Generator Fuel Level Switch Low | F12GE101 Fuel Level | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | XS12562 | XA12562 | 2000-F12-PID-PR-10002 | F12-DC-401 Primary Crusher 2 Dust Collector Alarm Feedback | F12DC401 Alarm | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  | TBC Vendor Details. | 2
|  |  |  | F12SW012HTY | F12SW012_HTY | N/A | F12-SW-012 Fuse Healthy | F12SW012 Fuse Healthy | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
|  |  |  | ZSC12014 | ZAC12014 | N/A | F12-TR-001 PRIMARY CRUSHING 415V MCC TRANSFORMER Enclosure Door Position Switch Closed | F12TR001 415VMCCDoor CL | Alarm | Normal | Alarm | Hardwired to PCS | 0 |  |  | 2
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 164 | 164

## 5. Totalisers
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CRUSHING
2000-F12-LST-PR-10001
TOTALISERS
Reset Period
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | Type | P&ID | Description | Abbreviated Description (Faceplate) | Units | Shift | Day | Cont | Comments | Rev
|  |  |  | WS12557 | WQI12557 | WQI | 2000-F12-PID-PR-10002 | F12-CV-402 Weightometer Totaliser | F12CV402 WeightTotaliser | tonnes (wet) | X | X | X | Running total of wet tonnes passing over Weightometer. Representation of crushing circuit total tonnes WS12557 Pulse Tonnes utilised for totaliser calculation | 2
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 1 | 1
1
Update PCT from IO list and contractor checks

## 6. OnOff Valves
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CRUSHING
2000-F12-LST-PR-10001
OPEN-CLOSE VALVES
Permissives and Trips
Area | Type | Loop No. | Suffix | Tag Name | P&ID | Valve Description | Abbreviated Description (Faceplate) | Valve Type | Fail Position | Manual | Auto | Open Condition (Auto Mode) | Close Condition (Auto Mode) | # | Condition | Description (if required) | Delay On | Delay Off | Open Permissive | Close Permissive | Open Interlock | Close Interlock | Bypass | Reset Required | Comments | Rev
|  |  |  | XV12005 | 2000-F12-PID-PR-10001 | F12-BN-401 Rom Bin Raw Water Valve | F12BN401 Dust Spray | DETAIL 7 | FC | X | X | ZI12005A < P_Lo OR ZI12005B < P_Lo | ZI12005A > P_Hi AND ZI12005B > P_Hi for 5 seconds | CT1 | XV12005 Opened for > 30 minutes | ROM Dust Sprays Open > 30mins | 1800 |  |  |  |  | X | X | X | Open condition is OR as Haul Truck on either side may be in dumping position. Close Auto Condition is AND as no haul trucks are present in order to stop dust suppression. | 2
|  |  |  | XV12006 | 2000-F12-PID-PR-10001 | F12-BN-405 Primary Crusher 2 Discharge Chamber Raw Water Valve | F12BN405 Water Spray | DETAIL 7 | FC | X | X | ZI12005A < P_Lo OR ZI12005B < P_Lo OR 12CG401_AMPS > P_Lo | (ZI12005A > P_Hi AND ZI12005B > P_Hi) OR 12CG401_AMPS < P_Lo for > 20 seconds | [12 empty] | 2
[5 empty] | 2000-F12-PID-PR-10001 | F12-FA-401 Primary Crusher 2 Discharge Apron Feeder Raw Water Valve | F12FA401 Water Spray | DETAIL 11 | FC | X | X | F12-FA-401 Running for 3 seconds. | F12-FA-401 Not Running for > 10 seconds | [12 empty] | 2
|  |  |  | SV12550 | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Tail End Raw Water Valve | F12CV402 Tail End Spray | DETAIL 11 | FC | X | X | F12-FA-401 Running for 75 seconds. | F12-CV-402 Not Running for > 3 seconds OR F12-FA-401 Not Running for > 75 seconds | [12 empty] | 2
|  |  |  | XV12551 | 2000-F12-PID-PR-10002 | F12-CV-402 Stockpile Feed Conveyor Head End Raw Water Valve | F12CV402 Head End Spray | DETAIL 7 | FC | X | X | F12-FA-401 Running for 150 seconds. | F12-CV-402 Not Running for > 3 seconds OR F12-FA-401 Not Running for > 150 seconds | [12 empty] | 2
|  |  |  | XV12259 | 2000-F12-PID-PR-10003 | F12-TK-423 Primary Crusher 2 Cooling Water Tank Feed Valve Solenoid | F12TK423 Top Up Water | DETAIL 7 | FC | X | X | LI12260 <= P_Lo | LI12260 >= P_Hi | [12 empty] | 1
|  |  |  | SV12090 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher 2 Mantle Lower Solenoid | F12CG401 Mantle Lower | VENDOR | N/A | X | X | F12-SEQ-0007 OR F12-SEQ-0005 | F12-SEQ-0006 OR F12-SEQ-0005 | OP1 | SV12089 NOT ENERGISED | Mantle Raise N_Energised | 0 |  | X | [5 empty] | Part of F12-CG-401 Primary Crusher 2 package. Valve can be opened during Primary Crusher 2 running and under load. Please refer to 2000-ME001.1-M02-50001 for details. Single digital output valve. | 1
[14 empty] | CT1 | F12PO404 AND F12PO405 Not Running | Lubrication Pump Not Running | 3 |  |  |  |  | X |  |  | During Mantle Raise or Lower operation, the lubrication pumps must be running. | 2
|  |  |  | SV12089 | 2000-F12-PID-PR-10001 |  | F12CG401 Mantle Raise | VENDOR | N/A | X | X | F12-SEQ-0006 OR F12-SEQ-0005 | F12-SEQ-0007 OR F12-SEQ-0005 | OP1 | SV12090 NOT ENERGISED | Mantle Lower N_Energised | 0 |  | X | [5 empty] | Part of F12-CG-401 Primary Crusher 2 package. Valve can be opened during Primary Crusher 2 running and under load. Please refer to 2000-ME001.1-M02-50001 for details. Single digital output valve. | 1
[6 empty] | F12-CG-401 Primary Crusher 2 Mantle Raise Solenoid | [7 empty] | CT1 | F12PO404 AND F12PO405 Not Running | Lubrication Pump Not Running | 3 |  |  |  |  | X |  |  | During Mantle Raise or Lower operation, the lubrication pumps must be running. | 2
|  |  |  | XV12122 | 2000-ME001.1-E02-50001 | F12-LU-401 Primary Crusher 2 Lubrication System Heat Exchanger Drain Valve Solenoid Valve Open | F12LU401 Lube System | VENDOR | N/A | X | X | Duty F12-PO-404/405 Not Running | Duty F12-PO-404/405 Running | [11 empty] | 2 x DI and 1 x DO valve. Refer to Digital Input and Digital Output sheet under tag number 12122 | 2
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
9
Update PCT from IO list and contractor checks

## 7. Control Valves
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CRUSHING
2000-F12-LST-PR-10001
CONTROL VALVES
Permissive and Trips
Area | Type | Loop No. | Suffix | Tag Name | P&ID | Valve Description | Abbreviated Description (Faceplate) | Valve Type | Fail Position | Manual | Auto | Open Condition (Auto Mode) | Close Condition (Auto Mode) | # | Condition | Description (if required) | Delay On | Delay Off | Open Permissive | Close Permissive | Open | Close | Bypass | Reset Required | Comments | Rev
|  |  |  | TCV12127 | 2000-F12-PID-PR-10001 | F12-TCV-12127 Primary Crusher 2 Oil Chiller Cooling Water Control Valve | F12LU401 Lube Coolng Wtr | DETAIL 1 | FO | X | X | [14 empty] | 0
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
1
Update PCT from IO list and contractor checks

## 8. PID Cont
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CRUSHING
2000-F12-LST-PR-10001
PID Controllers
[10 empty] | Modes |  |  |  | Setpoint |  |  | Range |  |  | Process Switchpoints | [11 empty] | Alarms | [8 empty] | Controlled/Manipulated Variable | [10 empty] | Comment | Rev
Area | Type | Loop No. | Suffix | Tag Source | Tag Name | P&ID | Controller Description | Abbreviated Description (Faceplate) | Normal Operating Mode | Manual | Auto | Cascade | Process Value Tag | Min | Max | Unit | Min | Max | Unit | P_LL | P_LL Delay ON (sec) | P_LL Delay OFF (sec) | P_Lo | P_Lo Delay ON (sec) | P_Lo Delay OFF (sec) | P_Hi | P_Hi Delay ON (sec) | P_Hi Delay OFF (sec) | P_HH | P_HH Delay ON (sec) | P_HH Delay OFF (sec) | A_LL | A_LL Delay (sec) | A_Lo | A_Lo Delay (sec) | A_Hi | A_Hi Delay (sec) | A_HH | A_HH Delay (sec) | Alarm Masking Conditions | Range Min | Range Max | Lower Limit | Upper Limit | Unit | Destination Description | Destination (Output) Tag | Direct / Reverse Acting | P | I | D
|  |  |  | TIT12127 | TIC12127 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher 2 Lube Oil Supply Temperature Transmitter | F12CG401 Lube Oil Ctrl | Automatic | X | X |  | TIT12127 | 30 | 42 | ℃ | 0 | 100 | ℃ |  |  |  | 35 | 5 |  | 41 | 5 | [8 empty] | 43 | 5 | 46 | 5 |  | 0 | 100 | 0 | 100 | % Open | Primary Crusher 2 Oil Chiller Water Pump Discharge Valve | TCV12127 | Direct |  |  |  | Controls modulating valve, TCV12127 on F12-PW-425/426 pump discharge. As temperature (PV) rises, controller opens TCV12127. Note this controller's PV is from cooled lube oil. When crusher is underload, it is assumed the returning lube oil will have warmed 10-15C. A_HH: Crusher tripped. A_Hi: Warning P_Lo and P_Hi act as switchpoints for Chiller and Cooling Water Pump On/Off. See Drives. | 0
|  |  |  | WIT12557 | WIC12557 | 2000-F12-PID-PR-10002 | F12-WD-402 Stockpile Feed Conveyor Belt Weigher Weightometer Controller | F12CV402 Mass Ctrl | Automatic | X | X |  | WIT12557 | 0 | 2650 | tph | 0 | 3500 | tph |  |  |  | 270 | 5 | [7 empty] | 1500 | 5 | 1800 | 5 | 3200 | 5 |  |  | Mask when F12-CV-402 is NOT RUNNING. | 0 | 100 | 40 | 100 | % | Primary Crusher 2 Discharge Apron Feeder VSD | F12-FA-401 Motor VSD | Reverse |  |  |  | Nominal = 2634 t/h Design = 3135 t/h Alarms based on design and need to be confirmed during commissioning. A_Hi: Warning A_Lo: Warning A_LL: Warning. No associated action. Controller to be configured such that controller output (MV) is held constant when F12-FA-401 is stopped and unheld when F12-FA-401 is started again. | 2
|  |  |  | YI12523 | YIC12523 | 2000-F12-PID-PR-10002 | F12-CAM-101 Crushing Circuit Particle Size Analyser P80 Controller | F12CG401 PSD p80 Ctrl | Automatic |  | X |  | YE12523 | 50 | 180 | mm | 0 | 200 | mm | [16 empty] | 180 | 5 |  |  | Mask when WIC12557 < P_Lo | ZIC12062_L1 | ZIC12062_H1 | 50 | 250 | mm | F12-CG-401 Primary Crusher 2 Closed Side Setting Controller | ZIC12062 | Reverse |  |  |  | FLS Particle Size Analyser Camera Indicator. Rolling /smoothed 10 minute average output of P80 in units of millimetres to be confirmed by Vendor Documentation (FLS). PV Input Tag: vision/camera-name/p80 Please see: 2000-SPC-CS-110001 for details. Deadband to be confirmed during commissioning. Nominal: 10mm. Same value for steady-state error such that controller. Set controller to be slow acting such that mantle position is adjusted every 10 minutes. | 2
|  |  |  | F12CALC10007 | ZIC12062 | 2000-F12-PID-PR-10001 | F12-CG-401 Primary Crusher 2 Mantle Controller | F12CG401 CSS Ctrl | Cascade | X | X | X | F12CALC10007 | 50 | 250 | mm | ZIC12062_L1 | ZIC12062_H1 | mm |  |  |  | DL = -35 | 0 |  | DL = 20 | 0 |  |  |  |  | DL = -50 | 5 | DL = -25 | 5 | DL = 12.5 | 5 | DL = 25 | 5 |  | RAISE | LOWER | RAISE AND ZIC12062.PV CANNOT GO BELOW ZIC12062 P_Lo. | LOWER | FUNCTION | MANTLE RAISE SWITCH MANTLE LOWER SWITCH | HS12062 RAISE / F12-SEQ-0006 HS12063 LOWER / F12-SEQ-0007 | Direct (if PV>SV, then raise; if PV<SV, then lower) |  |  |  | This controller will raise and lower the mantle to the set-point within an accuracy/deadband of greater than +/- 5mm in deviation using ZIC12062_PV as feedback. As per FLS I/O List 2000-ME001.1-F17-50001, the range and zero-point (contact point between mantle and shell) will be adjusted during Mantle Calibration Sequence (F12-SEQ-0005). ZI12061_H1 is part of this Sequence, which is used to calculate ZIC12062_H1 and ZIC12062_L1. Please refer to the Calculations tab. The alarm setpoints are specific to the CSS setting in that they are alarms for deviations from the setpoint. Deviation setpoint = DL. Process deviation = ZIC12062_PV - ZIC12062_SV When in AUTO, the controller is to initiate the control logic when (ZIC12062.SV ≠ ZIC12062.PV) == TRUE of greater than or equal to 5 mm to automatically adjust the mantle position. (The Controller will initiate and control F12-SEQ-0006/0007 as required to raise / lower mantle to the ZIC12062.SV. Programmers please integrate as part of the control logic). The mantle may be adjusted within the limits of ZIC12062 P_Lo and P_Hi whilst the Crusher is running and under load. The Crusher mantle may be adjusted outside of these limits when the crusher is not running. It is the Operators responsibility when adjusting the mantle position outside the process switchpoint limits to ensure the crushing chamber is clear of material. The alarm setpoints will notify the CRO if tramp material has passed and the mantle has lowered. The control logic stated above in bold will need to return the mantle back to the ZIC12062 set point value. If the Controller is in MANUAL, the CRO will need to manually raise/lower the mantle via the DCS graphic buttons HS12062/HS12063. Otherwise, a field-operator will need to manually depress physical buttons HS12062/HS12063 on the Primary Crusher Junction Box with Crusher in LOCAL mode. The Low Process Switchpoint is used to prevent the Operator from manually raising the Mantle too high (via HS12062) when the Crusher is under load, and to avoid mantle and concave contact and other potential risks such as stalling the Crusher. An on-delay of zero seconds has been specified. Please refer to F12-SEQ-0006 description for further details. The High Process Switchpoint is to prevent the Operator from lowering the Mantle too much (via HS12063), thus causing a larger CSS than the setpoint value. This also has a zero second on-delay. | 2
DO NOT DELETE THIS ROW INSERT NEW ROWS ABOVE
|  |  |  | 4 | 4
Update PCT from IO list and contractor checks

## 9. Drives
Tag Name | P&ID | Name | Drive Type | Speed Min | Speed Max | Speed Units | SP Lower Limit | SP Upper Limit | Current Max | Manual | Auto | Start Condition (Auto Mode) | Stop Condition (Auto Mode) | # |  | Delay On | Delay Off | Start Permissive | Process | Critical | Hardwired to Drive | Bypass | Reset Required | Comments | Rev
F12-CG-401 | 2000-F12-PID-PR-10001 | Primary Crusher 2 | VSD | 0 | 100 | % |  |  | 374.275 | X | X | F12-SEQ-0001 OR F12-SEQ-0003 | F12-SEQ-0002 OR F12-SEQ-0004 OR 12CG401_T3 Active | [10 empty] | MAIN DRIVE DELAYED STOP TIME IS REQUIRED IN STOPPING F12-CG-401 in AUTO. See 12CG401_T2 in Misc. Sheet. This applies for specified process interlocks. 12CG401_AMPS P_Lo = 34 Value to be confirmed during commissioning. | 2
[12 empty] | Started manually by Operator | Stopped manually by Operator | 1 | F12-CG-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F12-CG-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-CG-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-CG-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-CG-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-CG-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-CG-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | YA12050 Healthy | 0 |  | X |  |  |  | X |  | Siren to sound for 15 seconds before drive start. | 0
[14 empty] | 9 | LAL12111 Normal & Crusher Auto | 5 |  | X |  |  |  | X |  | Logic: LAL12111 Normal AND F12-CG-401 IN AUTO VENDOR Lube Reservoir Level greater than Low | 0
[14 empty] | 10 | LAL12081 Normal, Crusher Auto | 5 |  | X |  |  |  | X |  | Logic: LAL12081 Not Active AND F12-CG-401 IN AUTO VENDOR Hydraulic Reservoir Level less than Low | 0
[14 empty] | 11 | TI12128 < A_Hi | 5 |  | X |  |  |  | X |  | Logic: TI12128 < A_Hi VENDOR Return lube oil temperature less than high alarm setpoint | 0
[14 empty] | 12 | FI12071 > A_Lo And Crusher Auto | 5 |  | X |  |  |  | X |  | Logic: FI12071 > A_Lo AND F12-CG-401 IN AUTO VENDOR F12-CG-401 Primary Crusher Assembly Outer Eccentric Lube Flow Indicating Transmitter greater than Low alarm setpoint and Crusher in AUTO. Delayed stop. See MISC sheet for further information. | 0
[14 empty] | 13 | FI12072 > A_Lo And Crusher Auto | 5 |  | X |  |  |  | X |  | Logic: FI12072 > A_Lo AND F12-CG-401 IN AUTO VENDOR F12-CG-401 Primary Crusher Assembly Upper Eccentric Lube Flow Indicating Transmitter greater than Low alarm setpoint and Crusher in AUTO. Delayed stop. See MISC sheet for further information. | 0
[14 empty] | 14 | FI12073 > A_Lo And Crusher Auto | 5 |  | X |  |  |  | X |  | Logic: FI12073 > A_Lo AND F12-CG-401 IN AUTO VENDOR F12-CG-401 Primary Crusher Assembly Pinion Lube Flow Indicating Transmitter greater than Low alarm setpoint and Crusher in AUTO. Delayed stop. See MISC sheet for further information. | 0
[14 empty] | 15 | FI12074 > A_Lo And Crusher Auto | 5 |  | X |  |  |  | X |  | Logic: FI12074 > A_Lo AND F12-CG-401 IN AUTO. VENDOR F12-CG-401 Primary Crusher Assembly Countershaft Supply Flow Indicating Transmitter greater than Low alarm setpoint and Crusher in AUTO. Delayed stop. See MISC sheet for further information. | 0
[14 empty] | 16 | FI12075 > A_Lo And Crusher Auto | 5 |  | X |  |  |  | X |  | Logic: FI12075 > A_Lo AND F12-CG-401 IN AUTO. VENDOR F12-CG-401 Primary Crusher Assembly Inner Eccentric Supply Flow Indicating Transmitter great than Low alarm setpoint & Crusher in AUTO Delayed stop. See MISC sheet for further information. | 0
[14 empty] | 17 | FI12079 > A_Lo And Crusher Auto | 5 |  | X |  |  |  | X |  | Logic: FI12079 > A_Lo AND F12-CG-401 IN AUTO. VENDOR Dust Seal Flow greater than alarm setpoint low. | 0
[14 empty] | 18 | TI12068 < A_Hi | 5 |  | X |  |  |  | X |  | Logic: TI12068 < A_Hi VENDOR Countershaft Inboard Bearing temp below the alarm setpoint high | 2
[14 empty] | 19 | TI12067 < A_Hi | 5 |  | X |  |  |  | X |  | Logic: TI12067 < A_Hi VENDOR Countershaft Outboard bearing temp below the alarm setpoint high | 2
[14 empty] | 20 | TI12066 < A_Hi And Crusher Auto | 5 |  | X |  |  |  | X |  | TI12066 < A_Hi AND F12-CG-401 IN AUTO. VENDOR Eccentric Lower Temp lower than alarm setpoint high. | 0
[14 empty] | 21 | TI12065 < A_Hi And Crusher Auto | 5 |  | X |  |  |  | X |  | TI12065 < A_Hi AND F12-CG-401 IN AUTO. VENDOR Outer Eccentric Wear RingTemp lower than alarm setpoint high. | 0
[14 empty] | 22 | TI12064 < A_Hi And Crusher Auto | 5 |  | X |  |  |  | X |  | TI12064 < A_Hi AND F12-CG-401 IN AUTO. VENDOR Outer Eccentric Upper less than alarm setpoint high. | 0
[14 empty] | 23 | ZIC12062 < A_Hi And Crusher Auto | 5 |  | X |  |  |  | X |  | Logic: ZIC12062 < A_Hi AND F12-CG-401 IN AUTO VENDOR Mantle Position not High | 0
[14 empty] | 24 | ZIC12062 > A_Lo And Crusher Auto | 5 |  | X |  |  |  | X |  | Logic: ZIC12062 > A_Lo AND F12-CG-401 IN AUTO VENDOR Mantle Position not Low | 0
[14 empty] | 25 | Mantle Calibration Inactive | 5 |  | X |  |  |  | X |  | Logic: F12-SEQ-0005 Inactive VENDOR MANTLE CALIBRATION SEQUENCE IS NOT ACTIVE | 2
[14 empty] | 26 | Lube Pump Min Run Time Elapsed | 0 |  | X |  |  |  | X |  | Logic: 12LU401_T1 ELAPSED VENDOR Lubrication pump must run for 15 minutes prior to Crusher motor start. Please see MISC sheet for further details. | 2
[14 empty] | 27 | LALL12111 Closed & Crusher Auto | 12CG401_T2 |  |  | X |  |  | X |  | Logic: LALL12111 Active AND F12-CG-401 IN AUTO VENDOR Primary Crusher 2 Lube Oil Reservoir less than Low Low & Crusher in AUTO mode. Delayed stop. See MISC sheet for further information. | 2
[14 empty] | 28 | TI12128 >= A_HH | 12CG401_T2 |  |  | X |  |  | X |  | Logic: TI12128 >= A_HH VENDOR Primary Crusher 2 Lube Oil Return Temp greater than High High alarm setpoint & Crusher in AUTO mode. Delayed stop. See MISC sheet for further information. | 2
[14 empty] | 29 | FI12071 <= A_LL | 12CG401_T2 |  |  |  | X |  |  | X | Logic: FI12071 <= A_LL VENDOR F12-CG-401 Primary Crusher Assembly Outer Eccentric Lube Flow Indicating Transmitter PV less than Low-Low | 2
[14 empty] | 30 | FI12072 <= A_LL | 12CG401_T2 |  |  |  | X |  |  | X | Logic: FI12072 <= A_LL VENDOR F12-CG-401 Primary Crusher Assembly Upper Eccentric Lube Flow Indicating Transmitter PV less than Low-Low | 2
[14 empty] | 31 | FI12073 <= A_LL | 12CG401_T2 |  |  |  | X |  |  | X | Logic: FI12073 <= A_LL VENDOR F12-CG-401 Primary Crusher Assembly Pinion Lube Flow Indicating Transmitter PV less than Low-Low | 2
[14 empty] | 32 | FI12074 <= A_LL | 12CG401_T2 |  |  |  | X |  |  | X | Logic: FI12074 <= A_LL VENDOR F12-CG-401 Primary Crusher Assembly Countershaft Supply Flow Indicating Transmitter PV less than Low-Low | 2
[14 empty] | 33 | FI12075 <= A_LL | 12CG401_T2 |  |  |  | X |  |  | X | Logic: FI12075 <= A_LL VENDOR F12-CG-401 Primary Crusher Assembly Inner Eccentric Supply Flow Indicating Transmitter PV less than Low-Low | 2
[14 empty] | 34 | FI12079 <= A_LL | 12CG401_T2 |  |  |  | X |  |  | X | Logic: FI12079 <= A_LL VENDOR Dust Seal Flow lower than alarm setpoint low-low. | 2
[14 empty] | 35 | TI12068 >= A_HH And Crusher Auto | 12CG401_T2 |  |  | X |  |  | X |  | Logic: TI12068 >= A_HH AND F12-CG-401 IN AUTO VENDOR Countershaft Outboard Bearing Temp Delayed stop. See MISC sheet for further information. | 2
[14 empty] | 36 | TI12067 >= A_HH And Crusher Auto | 12CG401_T2 |  |  | X |  |  | X |  | Logic: TI12067 >= A_HH AND F12-CG-401 IN AUTO. VENDOR Countershaft Inboard Bearing Temp. Delayed stop. See MISC sheet for further information. | 2
[14 empty] | 37 | TI12064 >= A_HH And Crusher Auto | 5 |  |  |  | X |  |  | X | Logic: TI12064 >= A_HH AND F12-CG-401 IN AUTO. VENDOR F12-CG-401 Primary Crusher Assembly Inner Pinion Shaft Bearing Temperature Transmitter. | 2
[14 empty] | 38 | TI12065 >= A_HH And Crusher Auto | 5 |  |  |  | X |  |  | X | Logic: TI12065 >= A_HH AND F12-CG-401 IN AUTO. VENDOR F12-CG-401 Primary Crusher Assembly Center Pinion Shaft Bearing Temperature Transmitter. | 2
[14 empty] | 39 | TI12066 >= A_HH And Crusher Auto | 5 |  |  |  | X |  |  | X | Logic: TI12066 >= A_HH AND F12-CG-401 IN AUTO. VENDOR F12-CG-401 Primary Crusher Assembly Outer Pinion Shaft Bearing Temperature Transmitter. | 2
[14 empty] | 40 | F12BW401 N_Run And Crusher Auto | 12CG401_T2 |  |  | X |  |  | X |  | Logic: F12-BW-401 NOT RUNNING AND F12-CG-401 IN AUTO VENDOR Primary Crusher 2 Dust Seal Blower Not Running. Delayed stop. See MISC sheet for further information. | 2
[14 empty] | 41 | Spider Grease System Cycle Fault | 12CG401_T2 |  |  | X |  |  | X |  | Logic: F12LU402_T3 Active VENDOR Spider grease system fault. Please refer to MISC sheet for further details. | 2
[14 empty] | 42 | SI12059 <= A_LL | 5 |  |  |  | X |  |  | X | VENDOR F12-CG-401 Primary Crusher 2 Mantle Position Transmitter | 0
[14 empty] | 43 | ZIC12062 >= A_HH | 5 |  |  | X |  |  | X |  | VENDOR Primary Crusher 2 Mantle Position greater than High High Mantle may be raised outside of these limits when Crusher stopped. | 0
[14 empty] | 44 | ZIC12062 <= A_LL | 5 |  |  | X |  |  | X |  | VENDOR Primary Crusher 2 Mantle Position lower than Low Low. Mantle may be raised outside of these limits when Crusher stopped. | 0
[14 empty] | 45 | VI12057 >= A_HH | 10 |  |  |  | X |  |  |  | VENDOR F12-CG-401 Motor Load Bearing Vibration | 0
[14 empty] | 46 | VI12058 >= A_HH | 10 |  |  |  | X |  |  |  | VENDOR F12-CG-401 Motor Non-Load Bearing Vibration | 0
[14 empty] | 47 | LAH12201 Alarm | 3 |  |  |  | X |  |  |  | F12BN405 Level Switch High Alarm | 2
[14 empty] | 48 | LI12200 >= A_HH | 5 |  |  | X |  |  | X |  | F12BN405 Level High High. | C
[14 empty] | 49 | XI12019F Running | 3 |  |  | X |  |  | X |  | Trip Primary Crusher if Rock Breaker is Running. Bypassable under Operator discretion. | 2
[14 empty] | 50 | XI12019D N_Home | 3 |  |  | X |  |  | X |  | Trip Primary Crusher if Rock Breaker is not in the Home position. Bypassable under Operator discretion. | 2
[14 empty] | 51 | TIC12127 >= A_HH | 5 |  |  | X |  |  | X |  | Trip Primary Crusher if Cooling Water temperature is greater than High High setpoint. | 0
F12-PO-403 | 2000-ME001.1-E02-50001 | Primary Crusher 2 Hydraulic Pump 1 | DOL | [5 empty] | 13.253 | X | X | F12-SEQ-0005 OR F12-SEQ-0006 | F12-PO-403/10_T1 Active AND (F12-SEQ-0005 OR F12-SEQ-0006 NOT RUNNING).
[12 empty] | Started manually by Operator via Hydraulic HPU graphic Start/Stop buttons (Duty Hydraulic Pump to be selected) | Stopped manually by Operator via Hydraulic HPU graphic Start/Stop buttons | 1 | F12-PO-403 Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F12-PO-403 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-PO-403 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-PO-403 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-PO-403 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-PO-403 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-PO-403 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | F12-PO-410 Running | 3 |  |  |  | X |  |  |  | Standby pump is not running. | 2
[14 empty] | 9 | LAL12081 Normal And Auto | 3 |  | X |  |  |  | X |  | Logic: LAL12081 Normal And F12PO403 in Auto Start permissive for hydraulic reservoir level. | 2
[14 empty] | 10 | TI12080 > A_Lo And Auto | 5 |  | X |  |  |  | X |  | Logic: TI12080 > A_Lo And F12PO403 in Auto Start permissive for hydraulic reservoir temperature. | 2
[14 empty] | 11 | LALL12081 Closed | 3 |  |  |  | X |  |  |  | Hydraulic oil reservoir tank level low low | 2
[14 empty] | 12 | TI12080 <= A_LL | 5 |  |  |  | X |  |  |  | Hydraulic oil reservoir tank temperature Low Low | 2
[14 empty] | 13 | TI12080 >= A_HH | 5 |  |  |  | X |  |  |  | Hydraulic oil temperature high high | 2
[14 empty] | 14 | SV12090 Open | 5 |  |  |  | X |  |  |  | Solenoid Ports 2 & 3 connected . F12CG401 Mantle Lower Solenoid Valve Open | 2
F12-PO-410 | 2000-ME001.1-E02-50001 | Primary Crusher 2 Hydraulic Pump 2 | DOL | [5 empty] | 13.253 | X | X | F12-SEQ-0005 OR F12-SEQ-0006 | F12-PO-403/10_T1 Active AND (F12-SEQ-0005 OR F12-SEQ-0006 NOT RUNNING).
[12 empty] | Started manually by Operator via Hydraulic HPU graphic Start/Stop buttons (Duty Hydraulic Pump to be selected) | Stopped manually by Operator via Hydraulic HPU graphic Start/Stop buttons | 1 | F12-PO-410 Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[14 empty] | 2 | F12-PO-410 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-PO-410 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-PO-410 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-PO-410 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-PO-410 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-PO-410 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | F12-PO-403 Running | 3 |  |  |  | X |  |  |  | Standby pump not running. | 2
[14 empty] | 9 | LAL12081 Normal And Auto | 3 |  | X |  |  |  | X |  | Logic: LAL12081 Normal And F12PO410 in Auto Start permissive for hydraulic reservoir level. | 2
[14 empty] | 10 | TI12080 > A_Lo And Auto | 5 |  | X |  |  |  | X |  | Logic: TI12080 > A_Lo And F12PO410 in Auto Start permissive for hydraulic reservoir temperature. | 2
[14 empty] | 11 | LALL12081 Closed | 3 |  |  |  | X |  |  |  | Hydraulic oil reservoir tank level low low | 2
[14 empty] | 12 | TI12080 <= A_LL | 5 |  |  |  | X |  |  |  | Hydraulic oil reservoir tank temperature low low | 2
[14 empty] | 13 | TI12080 >= A_HH | 5 |  |  |  | X |  |  |  | Hydraulic oil temperature high high | 2
[14 empty] | 14 | SV12090 Open | 5 |  |  |  | X |  |  |  | Solenoid Ports 2 & 3 connected . F12CG401 Mantle Lower Solenoid Valve Open | 2
F12-PO-419 | 2000-ME001.1-E02-50001 | Primary Crusher 2 Spider Lubrication Pump | DOL | [5 empty] | 1.5417 | X | X | F12LU402_T1 (via XC12103 On) | XA12100 Active OR F12LU402_T2 Elapsing (via XC12103 Off) | [11 empty] | 2
[12 empty] | Started manually by Operator via Lubrication Pack graphic Start/Stop buttons (Duty Hydraulic Pump to be selected) (via XC12103 On) | Stopped manually by Operator via Lubrication Pack graphic Start/Stop buttons (via XC12103 Off) | 1 | F12-PO-419 Comms Failure | 0 |  |  |  | X |  |  |  |  | 0
[12 empty] | XC12103 Activated AND in LOCAL |  | 2 | F12-PO-419 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-PO-419 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-PO-419 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-PO-419 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-PO-419 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-PO-419 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | F12-CG-401 Not Running | 3 |  | X |  |  |  | X |  | VENDOR FLS specified. | 2
[14 empty] | 9 | HI12101B On | 5 | [7 empty] | Maintenance Field Selector Switch Active. | 2
F12-PO-404 | 2000-ME001.1-E02-50001 | Primary Crusher 2 Lubrication Pump 1 | DOL | [5 empty] | 1.5417 | X | X | F12-SEQ-0001 | 12LU401_T2 ELAPSED AND TI12128 < P_Lo == TRUE FOR 10 SECONDS | [10 empty] | STOP PERMISSIVE: 12LU401_T2 must elapse. | 2
[12 empty] | Started manually by Operator via Lubrication Pack graphic Start/Stop buttons (Duty Lubrication Pump to be selected) | Manually stopped by Operator. Prompt CRO if 12LU401_T2 Not Elapsed | 1 | F12-PO-404 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 2 | F12-PO-404 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-PO-404 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-PO-404 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-PO-404 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-PO-404 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-PO-404 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | F12-PO-405 Running | 30 |  |  |  | X |  |  |  | Standby pump running. Delay to allow pump changeover without stopping Crusher. Delay duration to be confirmed during commissioning. | 2
[14 empty] | 9 | LAL12111 Normal And Auto | 5 |  | X |  |  |  | X |  | Logic: LAL12111 Normal And F12-PO-404 in Auto Start permissive for lubrication reservoir level. | 2
[14 empty] | 10 | TI12110 >= P_Hi And Auto | 5 |  | X |  |  |  | X |  | Logic: TI12110 >= P_Hi and F12-PO-404 in Auto Must be greater than or equal to 30C to start when the drive is in Auto. | 2
[14 empty] | 11 | TI12110 < A_Lo And Auto | 60 |  |  |  | X |  |  |  | Logic: TI12110 < A_Lo And F12PO404 in Auto Interlock for running pump in Auto. Must be greater than A_Lo = 27C. | 2
[14 empty] | 12 | PDAH12121 Alarm | 300 |  |  |  | X |  |  |  | F12-LU-401 Lube Filters Differential Pressure | 2
[14 empty] | 13 | LALL12111 Active | 3 |  |  |  | X |  |  |  | Lube oil reservoir tank level low low. | 2
[14 empty] | 14 | TI12110 <= A_LL | 5 |  |  |  | X |  |  |  | Logic: TI12110 <= A_LL (MASK IF 12LU401_T3 NOT ELAPSED) Lube oil reservoir tank temperature low low. Cannot start pumps and therefore crusher until heaters raise lube oil to temperature SP. The interlock becomes applicable only after the 12LU401_T3 (Misc sheet) timer has elapsed. | 2
F12-PO-405 | 2000-ME001.1-E02-50001 | Primary Crusher 2 Lubrication Pump 2 | DOL | [5 empty] | 1.5417 | X | X | F12-SEQ-0001 | 12LU401_T2 ELAPSED AND TI12128 < P_Lo == TRUE FOR 10 SECONDS | [10 empty] | STOP PERMISSIVE: 12LU401_T2 must elapse. | 2
[12 empty] | Started manually by Operator via Lubrication Pack graphic Start/Stop buttons (Duty Lubrication Pump to be selected) | Stopped manually by Operator Prompt CRO if 12LU401_T2 Not Elapsed | 1 | F12-PO-405 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 2 | F12-PO-405 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-PO-405 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-PO-405 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-PO-405 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-PO-405 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-PO-405 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | F12-PO-404 Running | 30 |  |  |  | X |  |  |  | Standby pump running. Delay to allow pump changeover without stopping Crusher. Delay duration to be confirmed during commissioning. | 2
[14 empty] | 9 | LAL12111 Normal And Auto | 5 |  | X |  |  |  | X |  | Logic: LAL12111 Normal And F12-PO-405 in Auto Start permissive for lubrication reservoir level. | 2
[14 empty] | 10 | TI12110 >= P_Hi And Auto | 5 |  | X |  |  |  | X |  | Logic: TI12110 >= P_Hi and F12-PO-405 in Auto Must be greater than or equal to 30C to start when the drive is in Auto. | 2
[14 empty] | 11 | TI12110 < A_Lo And Auto | 60 |  |  |  | X |  |  |  | Logic: TI12110 < A_Lo And F12PO405 in Auto Interlock for running pump in Auto. Must be greater than A_Lo = 27C. | 2
[14 empty] | 12 | PDAH12121 Alarm | 300 |  |  |  | X |  |  |  | F12-LU-401 Lube Filters Differential Pressure | 2
[14 empty] | 13 | LALL12111 Active | 3 |  |  |  | X |  |  |  | Lube oil reservoir tank level low low. | 2
[14 empty] | 14 | TI12110 <= A_LL | 5 |  |  |  | X |  |  |  | Logic: TI12110 <= A_LL (MASK IF 12LU401_T3 NOT ELAPSED) Lube oil reservoir tank temperature low low. Cannot start pumps and therefore crusher until heaters raise lube oil to temperature SP. The interlock becomes applicable only after the 12LU401_T3 (Misc sheet) timer has elapsed. | 2
F12-BW-401 | 2000-ME001.1-E02-50001 | Primary Crusher 2 Dust Seal Blower | DOL | [5 empty] | 3.6145 | X | X | F12-SEQ-0003 | F12-SEQ-0004
[12 empty] | Manually started by Operator | Manually stopped by Operator | 1 | F12-BW-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-BW-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-BW-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-BW-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-BW-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-BW-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-BW-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F12-HT-401 | 2000-ME001.1-E02-50001 | PRIMARY CRUSHER 2 MOTOR SPACE HEATER | DOL | [5 empty] | 1.25 |  | X | F12-CG-401 NOT RUNNING | F12-CG-401 RUNNING
[14 empty] | 1 | F12-HT-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-HT-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-HT-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-HT-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-HT-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-HT-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-HT-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F12-HT-402 | 2000-F12-PID-PR-10001 | ROCKBREAKER HPU OIL HEATER | DOL | [5 empty] | TBC | X | X | Vendor PLC | Vendor PLC
[14 empty] | 1 | F12-HT-402 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-HT-402 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-HT-402 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-HT-402 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-HT-402 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-HT-402 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-HT-402 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F12-HU-402 | 2000-F12-PID-PR-10001 | ROCKBREAKER HPU | DOL | [5 empty] | 180.7229 | X | X | Started in LOCAL or REMOTE F12RB401 Start Request approved by CRO
[14 empty] | 1 | F12-HU-402 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-HU-402 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-HU-402 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-HU-402 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-HU-402 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-HU-402 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-HU-402 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F12-PW-425 | 2000-F12-PID-PR-10003 | PRIMARY CRUSHER 2 COOLING WATER PUMP 1 | DOL | [5 empty] | TBC | X | X | TIC12127 >= P_Hi AND DUTY F12-PO-404/405 RUNNING | TIC12127 <= P_Lo AND F12CU401 NOT RUNNING | [10 empty] | Cooling Water Pump to turn off after Chiller switches off when both are in auto.
[12 empty] | Manually started by Operator | Manually stopped by Operator | 1 | F12-PW-425 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-PW-425 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-PW-425 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-PW-425 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-PW-425 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-PW-425 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-PW-425 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | LI12260 <= A_LL | 5 |  |  |  | X |  |  | X | Primary Crusher 2 Cooling Water Tank Level Low Low | 2
[14 empty] | 9 | TCV12127 CLOSED | 5 |  |  | X |  |  | X |  |  | B
[14 empty] | 10 | ZIC12262 Closed | 3 |  |  |  | X |  |  |  | Suction Valve Closed. | 2
[14 empty] | 11 | ZIC12263 Closed | 3 |  |  |  | X |  |  |  | Discharge Valve Closed. | 2
[14 empty] | 12 | FALL12266 Active | 3 |  |  |  | X |  |  |  | Discharge flow switch alarm low low. | 2
F12-PW-426 | 2000-F12-PID-PR-10003 | PRIMARY CRUSHER 2 COOLING WATER PUMP 2 | DOL | [5 empty] | TBC | X | X | TIC12127 >= P_Hi AND DUTY F12-PO-404/405 RUNNING | TIC12127 <= P_Lo AND F12CU401 NOT RUNNING | [10 empty] | Cooling Water Pump to turn off after Chiller switches off when both are in auto.
[12 empty] | Manually started by Operator | Manually stopped by Operator | 1 | F12-PW-426 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-PW-426 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-PW-426 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-PW-426 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-PW-426 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-PW-426 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-PW-426 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | LI12260 <= A_LL | 5 |  |  |  | X |  |  | X | Primary Crusher 2 Cooling Water Tank Level Low Low | 2
[14 empty] | 9 | TCV12127 CLOSED | 5 |  |  | X |  |  | X |  |  | B
[14 empty] | 10 | ZIC12264 Closed | 3 |  |  |  | X |  |  |  | Suction Valve Closed. | 2
[14 empty] | 11 | ZIC12265 Closed | 3 |  |  |  | X |  |  |  | Discharge Valve Closed. | 2
[14 empty] | 12 | FALL12266 Active | 3 |  |  |  | X |  |  |  | Discharge flow switch alarm low low. | 2
F12-CU-401 | 2000-F12-PID-PR-10003 | PRIMARY CRUSHER 2 CHILLER | FE | [5 empty] | 96.2 | X | X | TIC12127 >= P_Hi AND DUTY F12-PO-404/405 RUNNING AND DUTY F12PW426/427 RUNNING (via HS12268STT) | TIC12127 <= P_Lo OR F12-PO-404 AND F12-PO-405 NOT RUNNING FOR 60 SECONDS (via HS12268STT)
[14 empty] | 1 | F12-CU-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-CU-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-CU-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-CU-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-CU-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-CU-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-CU-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | Duty Cooling Water Pump N_Rung | 3 |  |  |  | X |  |  |  | Logic: F12-PW-425 NOT RUNNING AND F12-PW-426 NOT RUNNING | 2
[14 empty] | 9 | HS12268 Start And Remote | 3 |  | X |  |  |  | X |  | Logic: HS12268 Start Command Issued And F12CU401 in Remote Auto | 2
F12-PS-401 | 2000-F12-PID-PR-10001 | PRIMARY CRUSHING 2 AREA SUMP PUMP | DOL SP | [5 empty] | 160 | X | X | LSH12370 Alarm | LSH12370 Normal for 5 seconds and 600 second timer elapsed
[12 empty] | Manually started by Operator | Manually stopped by Operator | 1 | F12-PS-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-PS-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-PS-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-PS-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-PS-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-PS-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-PS-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F12-FN-410 | 2000-F12-PID-PR-10001 | PRIMARY CRUSHER 2 BURIED VAULT VENTILATION FAN | DOL | [5 empty] | 51.4 | X | X | F12-SEQ-0001 | F12-SEQ-0002
[12 empty] | Manually started by Operator | Manually stopped by Operator | 1 | F12-FN-410 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-FN-410 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-FN-410 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-FN-410 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-FN-410 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-FN-410 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-FN-410 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F12-HT-41X | 2000-ME001.1-E02-50001 | PRIMARY CRUSHER 2 HYDRAULIC RESERVOIR HEATER 1 & 2 | DOL | [5 empty] | 4.8193 | X | X | TI12080 <= P_Lo | TI12080 >= P_Hi | [10 empty] | Common motor control for F12-HT-417 & 418 | 2
[14 empty] | 1 | F12-HT-417 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-HT-417 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-HT-417 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-HT-417 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-HT-417 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-HT-417 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-HT-417 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | LAL12081 Closed And Auto | 3 |  | X |  |  |  | X |  | Logic: LAL12081 Normal And F12HT417 in Auto Hydraulic tank level Low | 2
[14 empty] | 9 | LALL12081 Closed | 5 |  |  |  | X |  |  |  | Hydraulic tank level Low Low | 0
[14 empty] | 10 | TI12080 >= A_HH | 5 |  |  |  | X |  |  |  |  | B
F12-HT-418 | 2000-ME001.1-E02-50001 | PRIMARY CRUSHER 2 HYDRAULIC RESERVOIR HEATER 2 | DOL | [5 empty] | 4.8193 | X | X | TI12080 <= P_Lo | TI12080 >= P_Hi
[14 empty] | 1 | F12-HT-418 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-HT-418 Fail to Start / Stop | 0 |  |  |  | X |  |  | X |  | C
[14 empty] | 3 | F12-HT-418 Drive Fault | 0 |  |  |  | X |  |  | X |  | C
[14 empty] | 4 | F12-HT-418 E-Stop | 0 |  |  |  | X | X |  | X |  | C
[14 empty] | 5 | F12-HT-418 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-HT-418 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-HT-418 Drive Ready | 0 |  | X | [6 empty] | C
[14 empty] | 8 | LAL12081 Closed And Auto | 3 |  | X | [5 empty] | Logic: LAL12081 Normal And F12HT418 in Auto Hydraulic tank level low | 2
[14 empty] | 9 | LALL12081 Closed | 5 |  |  |  | X |  |  |  | Hydraulic tank level Low Low | 0
[14 empty] | 10 | TI12080 >= A_HH | 5 |  |  |  | X |  |  |  |  | B
F12-HT-419 | 2000-ME001.1-E02-50001 | PRIMARY CRUSHER 2 SPIDER DRUM HEATER | DOL | [5 empty] | 5 | X | X | TS12096 Active (Located on Heater) Nil Programming Required | TS12096 N_Active (Located on Heater) Nil Programming Required
[14 empty] | 1 | F12-HT-419 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-HT-419 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-HT-419 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-HT-419 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-HT-419 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-HT-419 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-HT-419 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F12-HT-40X | 2000-ME001.1-E02-50001 | PRIMARY CRUSHER 2 LUBRICATION RESERVOIR HEATER 1, 2, 3 & 4 | DOL | [5 empty] | 4.8193 | X | X | TI12110 <= P_Lo | TI12110 >= P_Hi | [10 empty] | Common motor control for F12-HT-407, 408, 409, 410 | 2
[14 empty] | 1 | F12-HT-407 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-HT-407 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-HT-407 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-HT-407 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-HT-407 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-HT-407 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-HT-407 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | LALL12111 Closed | 3 |  |  |  | X |  |  |  | Lube tank level less than Low Low | 2
[14 empty] | 9 | LAL12111 And Auto | 3 |  | X |  |  |  | X |  | Logic: LALL12111 Closed And F12HT407 In Auto Lube tank level less than Low | 2
[14 empty] | 10 | TI12110 >= A_HH | 5 |  |  |  | X |  |  |  | Lube tank temperature greater than High High SP. | B
F12-HT-408 | 2000-ME001.1-E02-50001 | PRIMARY CRUSHER 2 LUBRICATION RESERVOIR HEATER 2 | DOL | [5 empty] | 4.8193 | X | X | TI12110 <= P_Lo | TI12110 >= P_Hi
[14 empty] | 1 | F12-HT-408 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-HT-408 Fail to Start / Stop | 0 |  |  |  | X |  |  | X |  | C
[14 empty] | 3 | F12-HT-408 Drive Fault | 0 |  |  |  | X |  |  | X |  | C
[14 empty] | 4 | F12-HT-408 E-Stop | 0 |  |  |  | X | X |  | X |  | C
[14 empty] | 5 | F12-HT-408 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-HT-408 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-HT-408 Drive Ready | 0 |  | X | [6 empty] | C
[14 empty] | 8 | LALL12111 Closed | 3 |  |  |  | X |  |  |  | Lube tank level less than Low Low | 2
[14 empty] | 9 | LAL12111 And Auto | 3 |  | X | [5 empty] | Logic: LALL12111 Closed And F12HT408 In Auto Lube tank level less than Low | 2
[14 empty] | 10 | TI12110 >= A_HH | 5 |  |  |  | X |  |  |  | Lube tank temperature greater than High High SP. | B
F12-HT-409 | 2000-ME001.1-E02-50001 | PRIMARY CRUSHER 2 LUBRICATION RESERVOIR HEATER 3 | DOL | [5 empty] | 4.8193 | X | X | TI12110 <= P_Lo | TI12110 >= P_Hi
[14 empty] | 1 | F12-HT-409 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-HT-409 Fail to Start / Stop | 0 |  |  |  | X |  |  | X |  | C
[14 empty] | 3 | F12-HT-409 Drive Fault | 0 |  |  |  | X |  |  | X |  | C
[14 empty] | 4 | F12-HT-409 E-Stop | 0 |  |  |  | X | X |  | X |  | C
[14 empty] | 5 | F12-HT-409 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-HT-409 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-HT-409 Drive Ready | 0 |  | X | [6 empty] | C
[14 empty] | 8 | LALL12111 Closed | 3 |  |  |  | X |  |  |  | Lube tank level less than Low Low | 2
[14 empty] | 9 | LAL12111 And Auto | 3 |  | X | [5 empty] | Logic: LALL12111 Closed And F12HT409 In Auto Lube tank level less than Low | 2
[14 empty] | 10 | TI12110 >= A_HH | 5 |  |  |  | X |  |  |  | Lube tank temperature greater than High High SP. | B
F12-HT-410 | 2000-ME001.1-E02-50001 | PRIMARY CRUSHER 2 LUBRICATION RESERVOIR HEATER 4 | DOL HE | [5 empty] | 4.8193 | X | X | TI12110 <= P_Lo | TI12110 >= P_Hi
[14 empty] | 1 | F12-HT-410 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-HT-410 Fail to Start / Stop | 0 |  |  |  | X |  |  | X |  | C
[14 empty] | 3 | F12-HT-410 Drive Fault | 0 |  |  |  | X |  |  | X |  | C
[14 empty] | 4 | F12-HT-410 E-Stop | 0 |  |  |  | X | X |  | X |  | C
[14 empty] | 5 | F12-HT-410 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-HT-410 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-HT-410 Drive Ready | 0 |  | X | [6 empty] | C
[14 empty] | 8 | LALL12111 | 3 |  |  |  | X |  |  |  | Lube tank level less than Low Low | 2
[14 empty] | 9 | LAL12111 AND IN AUTO | 3 |  | X | [5 empty] | Logic: LALL12111 Closed And F12HT410 In Auto Lube tank level less than Low | 2
[14 empty] | 10 | TI12110 >= A_HH | 5 |  |  |  | X |  |  |  | Lube tank temperature greater than High High SP. | B
F12-FA-401 | 2000-F12-PID-PR-10001 | PRIMARY CRUSHER 2 DISCHARGE APRON FEEDER | VSD | 0 | 100 | % | 40 | 100 | 224 | X | X | LI12200 > P_Lo | LI12200 <= P_LoLo | [10 empty] | Vendor specified minimum speed: 2.7RPM. VSD ramp-up to be greater than 10 seconds to maximum speed. To be confirmed during commissioning. Reversing of drive to be limited to 10% of maximum forward speed during maintenance only. Source: 2000-ME004-M01-10001. | 1
[12 empty] | Manually started by Operator | Manually stopped by Operator | 1 | F12-FA-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-FA-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-FA-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-FA-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-FA-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-FA-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-FA-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | LI12200 <= A_LL | 5 |  |  | X |  |  | X |  | Discharge Chamber Level Low Low | C
[14 empty] | 9 | LI12199 <= A_LL | 5 |  |  | X |  |  | X |  | Discharge Chamber Level Low Low | C
[14 empty] | 10 | PWA12221A Alarm | 0 |  |  |  | X | X |  | X | Pullwire switch. | 0
[14 empty] | 11 | PWA12221B Alarm | 0 |  |  |  | X | X |  | X | Pullwire switch. | 0
[14 empty] | 12 | F12-CV-401 Not Running | 0 |  |  | X |  |  | X |  | Primary Crusher 2 Discharge Conveyor Not Running | 2
[14 empty] | 13 | LAH12227 Alarm | 3 |  |  | X |  |  | X |  | Apron Feeder Blocked Head Chute | 2
[14 empty] | 14 | YA12223 Healthy | 0 |  | X |  |  |  | X |  | Siren to sound prior to drive start. | 0
[14 empty] | 15 | SAL12222 Alarm | 3 |  |  |  | X |  |  | X | Mask for 10 seconds during startup. Set at less than or equal <= 2 RPM. To be confirmed during commissioning. | 2
[14 empty] | 16 | LI13002 >= A_Hi | 5 |  |  |  | X |  |  |  | Stockpile Level High. Begin running belts out. | 2
[14 empty] | 18 | 12LU441_T3 Active | 0 |  |  |  | X |  |  |  | Grease cycle switch not active during grease periods or low reservoir grease level for greater than 24 hours. See Misc. tab. | 2
[14 empty] | 19 | TI12228 >= A_HH | 5 |  |  |  | X |  |  |  | Gearbox Sump Cooler Temperature >= 90C. RTD. | 0
[14 empty] | 20 | TI12229 >= A_HH | 5 |  |  |  | X |  |  |  | Gearbox High Speed Bearing Temperature >= 90C. RTD | 0
[14 empty] | 21 | PA12231 Active | 30 |  |  |  | X |  |  |  | Gearbox Oil pressure switch low active | 0
[14 empty] | 22 | F12PO436 Not Running | 3 |  |  | X |  |  | X |  | Gearbox Oil Cooler Pump motor to be running prior to start-up of main motor drive. | 2
[14 empty] | 23 | TI12228 < P_Hi | 3 |  | X |  |  |  | X |  | Oil Temperature must be less than 70C to start Apron Feeder drive. | 2
F12-LU-441 | 2000-F12-PID-PR-10001 | PRIMARY CRUSHER 2 DISCHARGE APRON FEEDER AUTOLUBE GREASE SYSTEM | DOL | [5 empty] | 3 | X | X | 12LU441_T2 In Progress | 12LU441_T2 Inactive | [10 empty] | Manual mode for commissioning and maintenance purposes. | 2
[12 empty] | Manually started by Operator | Manually stopped by Operator | 1 | F12-LU-441 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-LU-441 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-LU-441 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-LU-441 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-LU-441 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-LU-441 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-LU-441 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | F12FA401 Not Running and Manual | 10 |  |  | X |  |  | X |  | Logic: F12FA401 Not Running and F12-LU-441 in Manual Bypass for commissioning purposes. Interlock if left in manual and feeder is not running. | 0
F12-FN-421 | 2000-F12-PID-PR-10001 | PRIMARY CRUSHER 2 DISCHARGE APRON FEEDER GEARBOX COOLER FAN | DOL | [5 empty] | 2.1 |  | X | TSH12237 Activated | TSH12237 Normal for 60 seconds | [10 empty] | On-delay 3 seconds for TSH12237. | 2
[14 empty] | 1 | F12-FN-421 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-FN-421 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-FN-421 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-FN-421 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-FN-421 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-FN-421 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-FN-421 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F12-PO-436 | 2000-F12-PID-PR-10001 | PRIMARY CRUSHER 2 DISCHARGE APRON FEEDER GEARBOX COOLER OIL PUMP | DOL | [5 empty] | 2.2 | X | X | F12-SEQ-0001 | F12-SEQ-0002 | [10 empty] | Pump to start prior to Apron Feeder Motor. Oil pressure to be > 0.7 bar and oil temperature < 70C prior to apron feeder motor energising. | 2
[14 empty] | 1 | F12-PO-436 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-PO-436 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-PO-436 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-PO-436 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-PO-436 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-PO-436 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-PO-436 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F12-CV-401 | 2000-F12-PID-PR-10002 | PRIMARY CRUSHER 2 DISCHARGE CONVEYOR | VSD | 0 | 100 | % | 100 | 100 | 581 | X | X | F12-SEQ-0001 | F12-SEQ-0002
[12 empty] | Manually started by Operator | Manually stopped by Operator | 1 | F12-CV-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-CV-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-CV-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-CV-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-CV-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-CV-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-CV-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | Sirens Healthy | 0 |  | X |  |  |  | X |  | Logic: YA12505A Healthy AND YA12505B Healthy AND YA12505C Healthy Siren to sound prior to drive start. | 0
[14 empty] | 9 | LAH12511 Alarm | 3 |  |  |  | X |  |  | X | Blocked chute switch on. | 2
[14 empty] | 10 | F12-RP-401 Not Running | 0 |  |  | X |  |  | X |  |  | 2
[14 empty] | 11 | F12-CV-402 Not Running | 0 |  |  | X |  |  | X |  |  | 2
[14 empty] | 12 | BDA12503A Alarm | 3 |  |  | X |  |  | X |  | Bypass for commissioning purposes. | 2
[14 empty] | 13 | BDA12503B Alarm | 3 |  |  | X |  |  | X |  | Bypass for commissioning purposes. | 2
[14 empty] | 14 | BDA12503C Alarm | 3 |  |  | X |  |  | X |  | Bypass for commissioning purposes. | 2
[14 empty] | 15 | BDA12503D Alarm | 3 |  |  | X |  |  | X |  | Bypass for commissioning purposes. | 2
[14 empty] | 16 | BDA12503E Alarm | 3 |  |  | X |  |  | X |  | Bypass for commissioning purposes. | 2
[14 empty] | 17 | BDA12503F Alarm | 3 |  |  | X |  |  | X |  | Bypass for commissioning purposes. | 2
[14 empty] | 18 | BRA12504 Alarm | 3 |  |  |  | X |  |  | X |  | 2
[14 empty] | 19 | PWA12501A Alarm | 0 |  |  |  | X | X |  | X |  | 0
[14 empty] | 20 | PWA12501B Alarm | 0 |  |  |  | X | X |  | X |  | 0
[14 empty] | 21 | PWA12501C Alarm | 0 |  |  |  | X | X |  | X |  | 0
[14 empty] | 22 | PWA12501D Alarm | 0 |  |  |  | X | X |  | X |  | 0
[14 empty] | 23 | ZSA12506A Alarm | 3 |  |  | X |  |  | X |  | Take-up switch (Upper) | 2
[14 empty] | 24 | ZSA12506B Alarm | 3 |  |  | X |  |  | X |  | Take-up switch (Lower) | 2
[14 empty] | 25 | VI12507A >= A_HH | 5 |  |  | X |  |  | X |  |  | B
[14 empty] | 26 | VI12507B >= A_HH | 5 |  |  | X |  |  | X |  |  | B
[14 empty] | 27 | LI13002 >= A_HH | 5 |  |  | X |  |  | X |  | COS 2 Level High High | 0
[14 empty] | 28 | SAL12510 Alarm | 3 |  |  |  | X |  |  | X | Mask for 10 seconds during startup. | 2
[14 empty] | 29 | F12-VR-401 Not Running | 3 |  |  | X |  |  | X |  |  | 2
[14 empty] | 30 | F12-FN-403 Not Running | 3 |  |  | X |  |  | X |  |  | 2
F12-RP-401 | 2000-F12-PID-PR-10002 | PRIMARY CRUSHER 2 ROOTPICKER | DOL | [5 empty] | 2.21 | X | X | F12-SEQ-0001 | F12-SEQ-0002 | [11 empty] | B
[14 empty] | 1 | F12-RP-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-RP-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-RP-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-RP-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-RP-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-RP-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-RP-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | LAH12511 Alarm | 3 |  |  | X |  |  | X |  | Blocked chute switch on. | 2
F12-FN-403 | 2000-F12-PID-PR-10002 | PRIMARY CRUSHER 2 DUST COLLECTOR FAN | DOL | [5 empty] | 59.6 | X | X | F12-SEQ-0001 | F12-SEQ-0002
[12 empty] | F12-SEQ-0003 |  | 1 | F12-FN-403 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[12 empty] | Manually started by Operator | Manually stopped by Operator | 2 | F12-FN-403 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-FN-403 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-FN-403 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-FN-403 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-FN-403 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-FN-403 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | PDI12542 >= A_HH | 3600 |  |  |  | X |  |  |  | Reclaim Dust Pressure Diff. Trip F12FN403 if PDI12542 >= A_HH for more than 1 hour as per vendor advice. | 0
[14 empty] | 9 | F12-VR-401 Not Running | 3 |  |  | X |  |  | X |  | Reclaim Dust Rotary Valve. Prevent start-up or trip Dust Collector Fan if Rotary Valve is Not Running. Bypass for maintenance testing purposes. | 2
[14 empty] | 10 | F12-CV-401 Not Running | 600 |  |  | X |  |  | X |  | Primary Crusher 2 Discharge Conveyor Not Running. | 2
F12-VR-401 | 2000-F12-PID-PR-10002 | PRIMARY CRUSHER 2 DUST COLLECTOR ROTARY VALVE | DOL | [5 empty] | TBC | X | X | F12-SEQ-0001 | F12-FN-403 STOPPED == TRUE FOR 5 MINUTES | [10 empty] | Vendor advice to stop Rotary Valve 3-5 minutes after Fan stopped.
[12 empty] | F12-SEQ-0003 |  | 1 | F12-VR-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-VR-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-VR-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-VR-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-VR-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-VR-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-VR-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | SAL12545 Alarm | 3 |  |  |  | X |  |  |  | Trip Rotary Valve if Low Speed Switch Active | 2
[14 empty] | 9 | F12CV401 Not Running | 5 |  |  | X |  |  | X |  | Primary Crusher 2 Discharge Conveyor Not Running | 2
F12-MG-401 | 2000-F12-PID-PR-10002 | PRIMARY CRUSHER 2 TRAMP MAGNET 1 | FE | [5 empty] | 161.21 | X | X | F12-SEQ-0001 | F12-SEQ-0002
[14 empty] | 1 | F12-MG-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-MG-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-MG-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-MG-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-MG-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-MG-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-MG-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | XA12519 Alarm | 3 |  |  |  | X |  |  | X | System Fault | 2
[14 empty] | 9 | XC12520 Active | 0 |  | X |  |  |  | X |  | Logic: XC12520 Active and F12MG401 in Remote Remote Select Not Active | 2
F12-MG-402 | 2000-F12-PID-PR-10002 | PRIMARY CRUSHER 2 TRAMP MAGNET 2 | FE | [5 empty] | 161.21 | X | X | F12-SEQ-0001 | F12-SEQ-0002
[14 empty] | 1 | F12-MG-402 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-MG-402 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-MG-402 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-MG-402 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-MG-402 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-MG-402 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-MG-402 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | XA12567 Alarm | 3 |  |  |  | X |  |  | X | System Fault | 2
[14 empty] | 9 | XC12568 Actove | 0 |  | X |  |  |  | X |  | Logic: XC12568 Active and F12MG402 in Remote Remote Select Not Active | 2
F12-RB-401 | 2000-F12-PID-PR-10001 | ROCKBREAKER | N/A | [5 empty] | TBC |  | X | Started in LOCAL or REMOTE F12RB401 Start Request approved by CRO | Vendor PLC | [10 empty] | See DI tab for details.
[14 empty] | 1 | F12-RB-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-RB-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-RB-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-RB-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-RB-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-RB-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-RB-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | F12-RB-401 Fault | 0 |  |  |  | X | X |  | X |  | B
[14 empty] | 9 | F12-CR-401 Running | 3 |  | X |  |  |  | X |  | Prevent starting of Rock Breaker if Crane in use. | 2
F12-FN-409 | 2000-F12-PID-PR-10001 | ROCKBREAKER HPU COOLING FAN | DOL | [5 empty] | TBC |  | X | Vendor PLC | Vendor PLC
[14 empty] | 1 | F12-FN-409 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-FN-409 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-FN-409 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-FN-409 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-FN-409 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-FN-409 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-FN-409 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F12-PO-402 | 2000-F12-PID-PR-10001 | ROCKBREAKER HPU HYDRAULIC PUMP | DOL | [5 empty] | TBC |  | X | Vendor PLC | Vendor PLC
[14 empty] | 1 | F12-PO-402 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-PO-402 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-PO-402 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-PO-402 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-PO-402 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-PO-402 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-PO-402 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
F12-CV-402 | 2000-F12-PID-PR-10002 | STOCKPILE FEED CONVEYOR | VSD | 0 | 100 | % | 100 | 100 | 581 | X | X | F12-SEQ-0001 | F12-SEQ-0002
[12 empty] | Manually started by Operator | Manually stopped by Operator | 1 | F12-CV-402 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-CV-402 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-CV-402 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-CV-402 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-CV-402 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-CV-402 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-CV-402 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | Sirens Healthy | 0 |  | X |  |  |  | X |  | Logic: YA12559A Healthy AND YA12559B Healthy Siren to sound prior to drive start. | 0
[14 empty] | 9 | LAHH13001 Active | 3 |  |  | X |  |  | X |  | COS 2 Level Switch High High | 2
[14 empty] | 10 | LI13002 >= A_HH | 5 |  |  | X |  |  | X |  | COS 2 Level High High | B
[14 empty] | 11 | BDA12555A Alarm | 3 |  |  | X |  |  | X |  | Bypass for commissioning purposes. | 2
[14 empty] | 12 | BDA12555B Alarm | 3 |  |  | X |  |  | X |  | Bypass for commissioning purposes. | 2
[14 empty] | 13 | BDA12555C Alarm | 3 |  |  | X |  |  | X |  | Bypass for commissioning purposes. | 2
[14 empty] | 14 | BDA12555D Alarm | 3 |  |  | X |  |  | X |  | Bypass for commissioning purposes. | 2
[14 empty] | 15 | BDA12555E Alarm | 3 |  |  | X |  |  | X |  | Bypass for commissioning purposes. | 2
[14 empty] | 16 | BDA12555F Alarm | 3 |  |  | X |  |  | X |  | Bypass for commissioning purposes. | 2
[14 empty] | 17 | BDA12555G Alarm | 3 |  |  | X |  |  | X |  | Bypass for commissioning purposes. | 2
[14 empty] | 18 | BDA12555H Alarm | 3 |  |  | X |  |  | X |  | Bypass for commissioning purposes. | 2
[14 empty] | 19 | BRA12556 Alarm | 3 |  |  |  | X |  |  | X |  | 2
[14 empty] | 20 | PWA12552A Alarm | 0 |  |  |  | X | X |  | X |  | 0
[14 empty] | 21 | PWA12552B Alarm | 0 |  |  |  | X | X |  | X |  | 0
[14 empty] | 22 | PWA12552C Alarm | 0 |  |  |  | X | X |  | X |  | 0
[14 empty] | 23 | PWA12552D Alarm | 0 |  |  |  | X | X |  | X |  | 0
[14 empty] | 24 | ZSA12558A Alarm | 3 |  |  | X |  |  | X |  |  | 2
[14 empty] | 25 | ZSA12558B Alarm | 3 |  |  | X |  |  | X |  |  | 2
[14 empty] | 26 | VI12560A >= A_HH | 5 |  |  | X |  |  | X |  |  | B
[14 empty] | 27 | VI12560B >= A_HH | 5 |  |  | X |  |  | X |  |  | B
[14 empty] | 28 | SAL12553 Alarm | 3 |  |  |  | X |  |  | X | Mask for 10 seconds during startup. | 2
[14 empty] | 29 | LAH12582 Alarm | 3 |  |  | X |  |  | X |  | Blocked chute detector. | 2
F12-CR-401 | 2000-F12-PID-PR-10001 | PRIMARY CRUSHER 2 OVERHEAD CRANE | FE | [5 empty] | 135 | X |  | Controlled by field operator via pendant | Controlled by field operator via pendant | [10 empty] | FC 24/10/24 : no control of crane | 2
[14 empty] | 1 | F12-CR-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-CR-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-CR-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-CR-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-CR-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-CR-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-CR-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | F12-RB-401 Running | 3 |  |  |  | X |  |  |  | Prevent use of crane if Rock Breaker is in use. | 2
F12-LE-401 | 2000-F12-PID-PR-10001 | PRIMARY CRUSHER 2 INSPECTION TROLLEY | FE | [5 empty] | 5.6 |  |  | Controlled by field operator via radio control | Controlled by field operator via radio control | [10 empty] | Fc 24/10/24 : no control of inspection trolley | 2
[14 empty] | 1 | F12-LE-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 2 | F12-LE-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-LE-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-LE-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-LE-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 6 | F12-LE-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | C
[14 empty] | 7 | F12-LE-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | F12-CG-401 Running | 5 |  |  | X |  |  | X |  | Primary Crusher 2 Running | 0
F12-HU-401 | 2000-F12-PID-PR-10001 | CRUSHING VAULT LOWER DOOR HYDRAULIC PUMP | DOL | [5 empty] | TBC | X
[14 empty] | 1 | F12-HU-401 Comms Failure | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 2 | F12-HU-401 Fail to Start / Stop | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 3 | F12-HU-401 Drive Fault | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 4 | F12-HU-401 E-Stop | 0 |  |  |  | X | X |  |  |  | 2
[14 empty] | 5 | F12-HU-401 MCC Unhealthy | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 6 | F12-HU-401 Drive Out of Service | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 7 | F12-HU-401 Drive Ready | 0 |  |  |  | X |  |  |  |  | 2
[14 empty] | 8 | LAL12202 Active | 5 |  |  | X |  |  | X |  | Hydraulic reservoir level low. | 2
39

## 10. Sequence
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CRUSHING
2000-F12-LST-PR-10001
SEQUENCES
Seq No. | Seq Description | Step | Action | Tag / Item | Description | Next Step Delay (s) | Step Advance Condition | Comments | Rev | Equipment Permissives | Recovery Seq. No if Step Faults
PLEASE REFER TO SEQUENCE FLOWCHART DOCUMENT (2000-F12-LST-PR-10002)

## 11. Calculation
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CRUSHING
2000-F12-LST-PR-10001
CALCULATIONS
|  |  | Unit | Inputs |  |  |  | Operator Input | Calc. Value | Manual Input
Tag Name | P&ID | Description (Software Tag Only) |  | # | Tag | Unit | Description |  |  | Nom | Min | Max | Calculation | Comments | Rev
F12CALC10001 | 2000-F12-PID-PR-10001 | F12LU401 Lube Temp Differential | ℃ | 1 | TI12127 | ℃ | Chilled Oil Supply to Crusher | [5 empty] | TDI12128 = TI12128 - TI12127 |  | 2
|  |  |  | 2 | TI12128 | ℃ | Lube Oil Return from Crusher | [7 empty] | B
|  |  |  | 3 | TDI12128 | ℃ | Oil Temperature Differential |  | X | [5 empty] | B
F12CALC10003 | 2000-F12-PID-PR-10001 | F12CG401 Number of Calibrations | count | [9 empty] | F12CALC0003 = F12CALC0003 + 1 | Calculation gets executed each time F12-SEQ-0005 is executed. Counter is resettable for new liner installation via Engineer login. | 2
[14 empty] | Present calculation in DCS Graphic for Operator reference. | 0
F12CALC10004 | 2000-F12-PID-PR-10001 | F12CG401 Time of Last CSS Calbrn | time | [9 empty] | F12CALC10004 = Controller Current System Time | Calculation is executed each time F12-SEQ-0005 is executed | 2
[14 empty] | Present calculation in DCS Graphic for Operator reference. | 0
F12CALC10005 | 2000-F12-PID-PR-10001 | F12CG401 Mantle RateofChange Low | Value (mm/s) | 1 | ZI12061.PV @ t=0 | mm | Mantle Position at rolling basis t=0s | [5 empty] | ZI12061.PV_MantleROC =[ ZI12061.PV(t=10s rolling) - ZI12061.PV(t=0s rolling) ] / (10 - 0) | Calculate rate of change over rolling 10 second basis. For input into F12-SEQ-0005. Sequence will time-out if mantle is moving reporting an ROC > 0 and issue an error. | 2
|  |  |  | 2 | ZI12061.PV @ t=10 | mm | Mantle Position at rolling basis t=10s | [7 empty] | C
|  |  |  | 3 | ZI12061.PV_MantleROC | mm/s | Mantle Position Change | [6 empty] | MantleROC parameter to be zero to indicate no change in mantle position. T=0s reference point to be taken when ROC = 0. | 0
F12CALC10006 | 2000-F12-PID-PR-10001 | F12CG401 Mantle RateofChange Hi | Value (mm/s) | 1 | ZI12061.PV @ t=0 | mm | Mantle Position at rolling basis t=0s | [5 empty] | ZI12061.PV_MantleROC =[ ZI12061.PV(t=2s rolling) - ZI12061.PV(t=0s rolling) ] / (2 - 0) | Calculate rate of change over rolling 2 second basis. For input into F12-SEQ-0005. Sequence will time-out if mantle is moving reporting an ROC > 0 and issue an error. | 2
|  |  |  | 2 | ZI12061.PV @ t=2 | mm | Mantle Position at rolling basis t=2s | [7 empty] | C
|  |  |  | 3 | ZI12061.PV_MantleROC | mm/s | Mantle Position Change | [6 empty] | MantleROC parameter to be zero to indicate no change in mantle position. T=0s reference point to be taken when ROC = 0. | 0
F12CALC10007 | 2000-F12-PID-PR-10001 | F12CG401 CSS | mm | [9 empty] | ZIC12062.PV = 457 * (ZI12061.PV - ZI12061_H1) / (0 - 457) for 0 =< ZI12061.PV =< 457 |  | 2
|  |  |  | 1 | ZI12061.PV | mm | F12CG401 Mantle Position | [6 empty] | Linear interpolation calculation using calibration concave / mantle contact point from F12-SEQ-0005 to adjust the range of ZIC12062. Zero point of ZIC12062 will vary based on liner wear and require calibration sequence to run to reflect accurate OSS value into controller. | C
|  |  |  | 2 | ZIC12062.PV | mm | F12CG401 CSS |  | X | [5 empty] | C
|  |  |  | 3 | ZI12061_H1 | mm | F12CG401 Mantle/Concave Contact (from F12-SEQ-0005). | [7 empty] | C
F12CALC10008 | 2000-F12-PID-PR-10001 | F12CG401 CSS Range High | mm | 1 | ZIC12062_H1 | mm | F12CG401 Range High |  | X |  |  |  | ZIC12062_H1 = 457 * (0 - ZI12061_H1) / (0 - 457) | Calculation inverts ZI12061 process value whereby the mantle and concave contact as determined during the Mantle Calibration Sequence. | 2
|  |  |  | 2 | ZI12061_H1 | mm | F12CG401 Mantle/Concave Contact (from F12-SEQ-0005). | [7 empty] | C
F12CALC10009 | 2000-F12-PID-PR-10001 | F12CG401 CSS Range Low | mm | 1 | ZIC12062_L1 | mm | F12CG401 Range Low |  | X |  |  |  | ZIC12062_L1 = 457 * (457 - ZI12061_H1) / (0 - 457) |  | 2
|  |  |  | 2 | ZI12061_H1 | mm | F12CG401 Mantle/Concave Contact (from F12-SEQ-0005). | [7 empty] | C
8 | 8

## 12. Misc
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CRUSHING
2000-F12-LST-PR-10001
MISC. INSTRUMENTS AND CONTROLLERS
Tag Name | P&ID | Description | Normal State | Alarm State | Hardwired (y/n) | Alarm Delay (secs) | Alarm Masking Conditions | Comments | Rev
12CG401_AMPS | 2000-F12-PID-PR-10001 |  | - | - | - | - | - | Primary Crusher 2 Amps Process Switchpoint, P_Lo = 34 Setpoint to be confirmed during commissioning. | 2
12CG401_T1 | 2000-F12-PID-PR-10001 | F12CG401 Mantle Calibration Timer | - | - | - | - | - | Timer that runs until the Gyratory Crusher Mantle Calibration sequence is initiated. Count in HOURS when 12CG401_AMPS is non-zero. Reset timer after 2000-F12-SEQ-0005 has run. | 2
12CG401_T2 | 2000-F12-PID-PR-10001 | F12CG401 Stop Delay Time | - | - | - | - | - | Please see 2000-ME001.1-M02-50001 Section 7.1 for further details. Start timer when Crusher Main Drive is initiated to stop via sequence F12-SEQ-0002 OR a relevant interlock is true (see Drives sheet). When Crusher Drive in AUTO, this timer must elapse before crusher drive may be stopped. Traffic lights on ROM will change to Red when this timer is active. Provide CRO option to cancel this timer if it is in progress. DEFAULT SETTING: 15 SECONDS. OPERATOR CONFIGURABLE RANGE: 15 - 120 SECONDS. | 2
12CG401_T3 | 2000-F12-PID-PR-10001 | F12CG401 Idle Time | - | - | - | - | - | Please see 2000-ME001.1-M02-50001 Section 7.1 for further details. Start timer when Crusher Main Drive Amps is equal to or less than P_Lo (Logic: F12CG401_AMPS <= P_Lo). The value of P_Lo is to be confirmed during commissioning. For design: F12CG401_AMPS P_Lo = 34 Timer: DEFAULT SETTING: 3600 SECONDS. OPERATOR CONFIGURABLE RANGE: 1800 - 3600 SECONDS. Activate 12CG401_T3 if Timer elapses. Timer will stop F12CG401 when in Auto. Timer will stop and reset if condition above is not met. | 2
12LU401_T1 | 2000-ME001.1-E02-50001 | F12PO404/405 Lube Oil Startup | - | - | - | - | - | Prior to starting F12CG401, the lubrication system shall run for 15 minutes to warm internal components. Duty lubrication pump to run for 15 minutes. Start on delay timer when F12-PO-404 OR F12-PO-405 running FLS Ref: Lubrication Run Time Timer duration: 15 minutes. Non-adjustable. Please see 2000-ME001.1-M02-50001 Section 7.1 for further details. | 2
12LU401_T2 | 2000-ME001.1-E02-50001 | F12PO404/405 Lube Oil Stop | - | - | - | - | - | Timer duration: 30 minutes MINIMUM. Adjustable greater than 30 minutes only. Auto-start timer when F12CG401 Drive confirmed Not Running. FLS Ref: Lubrication Delayed Stop Please see 2000-ME001.1-M02-50001 Section 7.1 for further details. | 2
12LU401_T3 | 2000-ME001.1-E02-50001 | F12PO404/405 Tank Temperature | Inactive | - | - | - | - | Temperature interlock mask for the start up of the Duty Lubrication Pump F12PO404/405. Start timer when Duty F12-PO-404 OR F12-PO-405 is started. When timer elapses, relevant interlock masks are to deactivate (refer to F12-PO-404 and F12-PO-405 on Drives sheet). FLS Ref: Tank Temperature L2 Delay Timer duration: 300 seconds. Non-adjustable. Please see 2000-ME001.1-M02-50001 Section 7.1 for further details. | 2
F12LU402_T1 | 2000-ME001.1-E02-50001 | Spider Grease Run Timer (Master) | N_Activated | - | N | - | - | Timer is started by F12-SEQ-0001 OR manually via a graphic start button on the faceplate for the Spider Grease System (F12-LU-401) within DCS: When F12LU402_T1 ELAPSES, • Start F12PO419 AND • Reset and restart F12LU402_T1 timer AND • Start F12LU402_T2 AND • Start F12LU402_T3 (or resume if timer already started in previous cycle). The Timer is stopped by F12-SEQ-0002 OR manually via a graphic stop button on the faceplate for the Spider Grease System (F12-LU-401) on the DCS. If Primary Crusher 2 (F12-CG-401) stops or trips, then this Timer (and therefore F12-LU-402) should also stop. FLS Ref: Grease Cycle Period Grease Cycle Period Range = 60 - 1500 seconds (Engineer login configurable). Grease Cycle Period Default = 150 seconds. Please refer to 2000-ME001.1-M02-50001 for further details. | 2
F12LU402_T2 | 2000-ME001.1-E02-50001 | Spider Cycle Fault Timer | N_Activated | Activated | N | 0 | - | Timer is the maximum F12PO419 permissible run time in a cycle. Start F12LU402_T2 when F12LU402_T1 elapses. If F12LU402_T2 ELAPSES then STOP F12PO419, OR stop and reset timer if XI12100 is active. Grease Cycle Fault Alarm (F12LU402_T2A) needs to latch until XI12100 becomes active (a successful grease cycle occurs). FLS Ref: Grease Cycle Fault Grease Cycle Fault Timer: 15 seconds non-adjustable. Please refer to 2000-ME001.1-M02-50001 for further details. | 2
F12LU402_T2A | 2000-ME001.1-E02-50001 | Grease Cycle Fault Alarm | N_Activated | Activated | N |  |  | Alarm generated from F12LU402_T2 elapsed. | 2
F12LU402_T3 | 2000-ME001.1-E02-50001 | Spider Lube Fault Timer | N_Activated | Activated | N | 0 | - | Start F12LU402_T3 when F12LU402_T1 elapses. When 12LU401_T3 elapses (completes 1500s), • Trip F12CG401 AND • Stop 12LU401_T1 AND • Activate LOCAL indicator light XI12102. Timer to stop and reset to 0 when activated. Spider Lube Fault Alarm (F12LU402_T3A) needs to latch until XI12100 becomes active (a successful grease cycle occurs). FLS Ref: Spider Lube Fault Spider Lube Fault Time: 1800 seconds Engineer adjustable only. Please refer to 2000-ME001.1-M02-50001 for further details. | 2
F12LU402_T3A | 2000-ME001.1-E02-50001 | Spider Lube Fault Alarm | N_Activated | Activated | N |  |  | Alarm generated from F12LU402_T3 elapsed. | 2
12PO403_10T1 | 2000-ME001.1-E02-50001 | Hydraulic Pump Min. Runtime | Inactive | - | N | - | - | Duty Hydraulic Pump to run for 35 minutes until shut off in Auto mode. Please see Drives sheet. Activate Timer when Duty Hydraulic Pump is started. When timer elapses, activate Misc Tag / bit such that F12-PO-403/10_T1 = ACTIVE. Stop and reset Timer if Hydraulic Pump is stopped before timer elapses. | 2
12BN401_DUMP | 2000-F12-PID-PR-10001 | F12BN401 2 Trucks Dump | Inactive | - | N | 5 | - | ALARM IF (ZI12005A =< P_Hi AND ZI12005B =< P_Hi) == TRUE. | 2
12LU441_T1 | 2000-F12-PID-PR-10001 | F12FA401 Grease Cycle Timer | Inactive | - | N | - | - | Source: 2000-ME004-M01-10001. Timer is started (or resumed) by the following conditions: - F12-SEQ-0001 OR - Manually via a graphic button on the DCS OR - F12-FA-401 Running (Group Start) OR - 12LU441_T2 Elapsed. When 12LU441_T1 ELAPSES, • Start 12LU441_T2 The Timer is paused if: - F12-SEQ-0002 Initiated - Manually via a graphic button on the DCS. - If Apron Feeder (F12-FA-401) stops or trips, then this Timer (and therefore F12-LU-441) should also pause. Timer Settings: DEFAULT SETTING: 4680 SECONDS. ENGINEER CONFIGURABLE RANGE: 3000 - 6000 SECONDS. | 2
12LU441_T2 | 2000-F12-PID-PR-10001 | F12FA401 Grease Cycle On Timer | Inactive | - | N | - | - | Source: 2000-ME004-M01-10001. Timer is started by 12LU441_T1 Elapsing. Timer will start F12-LU-441 to start greasing. When timer elapses, 12LU441_T1 will restart to continue grease cycle. The Timer is paused if: - F12-SEQ-0002 Initiated - Manually via a graphic button on the DCS (same as T1 timer) - If Apron Feeder (F12-FA-401) stops or trips, then this Timer (and therefore F12-LU-441) should also pause. Timer Settings: DEFAULT SETTING: 120 SECONDS. ENGINEER CONFIGURABLE RANGE: 10 - 600 SECONDS. | 2
12LU441_T3 | 2000-F12-PID-PR-10001 | F12FA401 24Hr Fault Timer | Inactive | - | N | - | - | Source: 2000-ME004-M01-10001. Grease cycle switch not active during grease periods or low reservoir grease level for greater than 24 hours. Timer is started if: - XS12224 Inactive (Not Pulsing) AND F12-LU-441 Running OR - LAL12225 Active Timer Settings: DEFAULT SETTING: 86400 SECONDS ENGINEER CONFIGURABLE RANGE: 3600 - 86400 SECONDS. When timer elapses, activate bit (Activate 12LU441_T3). 12LU441_T3 = ACTIVE is interlocked to the apron feeder. Stop and reset timer when - XS12224 Active AND F12-LU-441 Running AND - LAL12225 Inactive | 2
12RB401_R1 | 2000-F12-PID-PR-10001 | F12RB401 Start Request | Inactive | - | N | - | - | When Rock Breaker is attempted to be started either in LOCAL or REMOTE modes, prompt to appear in DCS "Approve use of Rock Breaker, note Primary Crusher 2 will interlock to stop << YES >> << CANCEL >>". Rock Breaker will be locked out unless this is selected true. Refer to Digital Input sheet for details. | 2
ZIC12062_L1 | 2000-F12-PID-PR-10001 | F12CG401 Range Low | - | - | - | - | - | Variable for output from Calculation. See 11. Calculation for further information. | C
ZIC12062_H1 | 2000-F12-PID-PR-10001 | F12CG401 Range High | - | - | - | - | - | Variable for output from Calculation. See 11. Calculation for further information. | C
ZI12061_H1 | 2000-F12-PID-PR-10001 | F12CG401 Concave/Mantle Contact | - | - | - | - | - | Determined and stored from F12-SEQ-0005 Mantle Calibration Sequence. Input into F12CALC10007/8/9 to determine ZIC12062.PV and Range Lower & Upper limits. | 2
12AN407_P80 | 2000-F12-PID-PR-10002 | F12AN407 p80 Rolling Average | - | - | - | - | - | Miscellaneous tag: Calculate Rolling Average from Tag Input on 30 minute basis. Tag Input: YE12523 p80. See FLS PVX IOM Manual for further details on FLS PlantVision Camera. | 2
XV12005_ALM | 2000-F12-PID-PR-10001 | XV12005 ROM Open 30min | - | - | - | - | - | Timer: 30 minutes (1800s) Engineer login Configurable. Start timer when XV12005 = Open. Stop and reset timer when XV12005 = Closed. Activate bit/alarm if XV12005 Open when timer elapses. | 2
23

## 13. Alarm Database
KCGM GROWTH PROJECT
PROCESS CONTROL TABLES - CRUSHING
2000-F12-LST-PR-10001
ALARM DATABASE
Tag Name | P&ID | Abbreviated Description (Faceplate) | Type | Alarm State | Alarm Value | Alarm Units | On Delay (sec) | Alarm Masking Condition | Impact | Urgency | Priority | Operator Response | Rev
F12LU402_T2A | 2000-ME001.1-E02-50001 | Grease Cycle Fault Alarm | Digital | Activated |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of grease cycle fault. | 2
F12LU402_T3A | 2000-ME001.1-E02-50001 | Spider Lube Fault Alarm | Digital | Activated |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Crusher tripped. Operator to investigate spider grease system before restart. | 2
XV12005_ALM | 2000-F12-PID-PR-10001 | XV12005 ROM Open 30min | Digital | Activated |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to place XV12005 in manual and close valve as excessive water has been emptied into ROM Bin. | 2
F12SW012SOP01 | 2000-F12-PID-PR-10001 | F12SwBrd P1 Iso Open | Digital | Alarm |  |  | 0 |  | None | Not Urgent (>30 minutes) | No Alarm | No response required. | 2
F12SW012SCL01 | 2000-F12-PID-PR-10001 | F12SwBrd P1 Iso Clsd | Digital | Alarm |  |  | 0 |  | None | Not Urgent (>30 minutes) | No Alarm | No response required. | 2
F12SW012SFH01 | 2000-F12-PID-PR-10001 | F12SwBrd P1 Fuse Healthy | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate in-field. | 2
F12SW012SOP02 | 2000-F12-PID-PR-10001 | F12SwBrd P2 Breaker Open | Digital | Alarm |  |  | 0 |  | None | Not Urgent (>30 minutes) | No Alarm | No response required. | 2
F12SW012SCL02 | 2000-F12-PID-PR-10001 | F12SwBrd P2 Breaker Clsd | Digital | Alarm |  |  | 0 |  | None | Not Urgent (>30 minutes) | No Alarm | No response required. | 2
F12SW012STR02 | 2000-F12-PID-PR-10001 | F12SwBrd P2 Breaker Trip | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate in-field. | 2
F12SW012SOP03 | 2000-F12-PID-PR-10001 | F12SwBrd P3 Cont Open | Digital | Alarm |  |  | 0 |  | None | Not Urgent (>30 minutes) | No Alarm | No response required. | 2
F12SW012SCL03 | 2000-F12-PID-PR-10001 | F12SwBrd P3 Cont Clsd | Digital | Alarm |  |  | 0 |  | None | Not Urgent (>30 minutes) | No Alarm | No response required. | 2
F12SW012SFH03 | 2000-F12-PID-PR-10001 | F12SwBrd P3 Fuse Healthy | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate in-field. | 2
F12SW012SOP04 | 2000-F12-PID-PR-10001 | F12SwBrd P4 Breaker Open | Digital | Alarm |  |  | 0 |  | None | Not Urgent (>30 minutes) | No Alarm | No response required. | 2
F12SW012SCL04 | 2000-F12-PID-PR-10001 | F12SwBrd P4 Breaker Clsd | Digital | Alarm |  |  | 0 |  | None | Not Urgent (>30 minutes) | No Alarm | No response required. | 2
F12SW012STR04 | 2000-F12-PID-PR-10001 | F12SwBrd P4 Breaker Trip | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate in-field. | 2
F12SW012SOP05 | 2000-F12-PID-PR-10001 | F12SwBrd P5 Breaker Open | Digital | Alarm |  |  | 0 |  | None | Not Urgent (>30 minutes) | No Alarm | No response required. | 2
F12SW012SCL05 | 2000-F12-PID-PR-10001 | F12SwBrd P5 Breaker Clsd | Digital | Alarm |  |  | 0 |  | None | Not Urgent (>30 minutes) | No Alarm | No response required. | 2
F12SW012STR05 | 2000-F12-PID-PR-10001 | F12SwBrd P5 Breaker Trip | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to investigate in-field. | 2
UI12010 | 2000-F12-PID-PR-10001 | F12 11kV Switchroom | Analogue | A_Hi | 30 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to investigate air conditioning and cause of high room temperatures. | 1
UI12012 | 2000-F12-PID-PR-10001 | F12 415V MCC Transf Room | Analogue | A_Hi | 30 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to investigate air conditioning and cause of high room temperatures. | 1
F12FIP001_ALM | 2000-F12-PID-PR-10001 | F12SwRoom Fire Alarm | Digital | Alarm |  |  | 0 |  | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k | Rapid (>5 to <15 minutes) | Urgent | Fire alarm Crushing Area Switchroom. Follow site specific Fire Emergency Plan. | 2
F12FIP001_FLT | 2000-F12-PID-PR-10001 | F12SwRoom Fire Fault | Digital | Alarm |  |  | 0 |  | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k | Rapid (>5 to <15 minutes) | Urgent | Fire alarm fault Crushing Area Switchroom. Follow site specific Fire Emergency Plan. | 2
F12SW001_OP | 2000-F12-PID-PR-10001 | F12 MCC Breaker Opn | Digital | Alarm |  |  | 0 |  | None | Not Urgent (>30 minutes) | No Alarm | No response required. | 2
F12SW001_CL | 2000-F12-PID-PR-10001 | F12 MCC Breaker Clsd | Digital | Alarm |  |  | 0 |  | None | Not Urgent (>30 minutes) | No Alarm | No response required. | 2
F12SW001_TRP | 2000-F12-PID-PR-10001 | F12 MCC Breaker Trip | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate in-field. | 2
F12SW001_SD | 2000-F12-PID-PR-10001 | F12 MCC Incomer Healthy | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate in-field. | 2
F12SW001_AF | 2000-F12-PID-PR-10001 | F12 MCC ArcFlash Healthy | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate in-field. | 2
F12DCS401_PS1 | 2000-F12-PID-PR-10001 | F12 DCS Pwr Healthy | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate in-field. | 2
F12BC001_FL3 | 2000-F12-PID-PR-10001 | F12SwRm 48V Charger | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate in-field. | 2
F12SR001_ESTP | 2000-F12-PID-PR-10001 | F12SwRm Emerg Shut Hlthy | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate in-field. | 2
UI12011 | 2000-F12-PID-PR-10001 | F12 415V Switchroom | Analogue | A_Hi | 30 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Prompt (>15 to <30 minutes) | Low | Operator to investigate air conditioning and cause of high room temperatures. | 1
F12UPS002ALM | 2000-F12-PID-PR-10001 | F12SwRm 240VAC UPS Alarm | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate in-field. | 2
LI12004A | 2000-F12-PID-PR-10001 | F12BN401 ROM Bin Lvl A | Analogue | A_Hi | 80 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to ensure traffic light system is in AUTO to suspend haul truck dumping until dumping pocket level lowers via Primary Crusher 2 operation. | C
LI12004B | 2000-F12-PID-PR-10001 | F12BN401 ROM Bin Lvl B | Analogue | A_Hi | 80 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to ensure traffic light system is in AUTO to suspend haul truck dumping until dumping pocket level lowers via Primary Crusher 2 operation. | C
ZI12005A | 2000-F12-PID-PR-10001 | F12BN401 Truck Pos. 1 | Analogue | A_Lo | 3 | m | 900 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate radar & water sprays ON/OFF. | B
ZI12005B | 2000-F12-PID-PR-10001 | F12BN401 Truck Pos. 2 | Analogue | A_Lo | 3 | m | 900 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate radar & water sprays ON/OFF. | B
XI12019G | 2000-F12-PID-PR-10001 | F12RB401 Breaker Fault | Digital | Activated |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Rock Breaker tripped. Operator to investigate on package HMI. | 2
VI12057 | 2000-F12-PID-PR-10001 | F12CG401 Mtr D/E Brg | Analogue | A_Hi | 3 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate bearing. | 0
VI12057 | 2000-F12-PID-PR-10001 | F12CG401 Mtr D/E Brg | Analogue | A_HH | 5 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate bearing. | C
VI12058 | 2000-F12-PID-PR-10001 | F12CG401 Mtr NDE Brg | Analogue | A_Hi | 3 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate bearing. | 0
VI12058 | 2000-F12-PID-PR-10001 | F12CG401 Mtr NDE Brg | Analogue | A_HH | 5 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate bearing. | C
SI12059 | 2000-F12-PID-PR-10001 | F12CG401 C/Shaft | Analogue | A_LL | 100 | RPM | 5 | Mask when F12-CG-401 is Not Running. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | B
SI12059 | 2000-F12-PID-PR-10001 | F12CG401 C/Shaft | Analogue | A_Lo | 120 | RPM | 5 | Mask when F12-CG-401 is Not Running. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate cause of low countershaft rotational speed. | 0
SI12060 | 2000-F12-PID-PR-10001 | F12CG401 M/Shaft | Analogue | A_Hi | 20 | RPM | 5 | Mask when F12-CG-401 is Not Running. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate. | B
ZI12061 | 2000-F12-PID-PR-10001 | F12CG401 Mantle Pos Phys | Analogue | A_Hi | 450 | mm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate. Mantle position may be adjusted in LOCAL. Operator response circumstantial. | C
ZIC12062 | 2000-F12-PID-PR-10001 | F12CG401 CSS Ctrl | Analogue | A_LL | DL = -50 | mm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | 0
ZIC12062 | 2000-F12-PID-PR-10001 | F12CG401 CSS Ctrl | Analogue | A_Lo | DL = -25 | mm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate mantle position. | 0
ZIC12062 | 2000-F12-PID-PR-10001 | F12CG401 CSS Ctrl | Analogue | A_Hi | DL = 12.5 | mm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate mantle position. May be due to tramp material passing through crusher and forcing hydraulic accumulator PRV to open to allow tramp material to pass. If so, Operator to place ZIC12062 in AUTO to allow Mantle Positioning System control logic to return Mantle to set value position or manually correct mantle position. | 0
ZIC12062 | 2000-F12-PID-PR-10001 | F12CG401 CSS Ctrl | Analogue | A_HH | DL = 25 | mm | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | 0
TI12064 | 2000-F12-PID-PR-10001 | F12CG401 Outr Ecc Upper | Analogue | A_Hi | 54 | ℃ | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate Lubrication Oil temperature & Oil Chiller circuit. | B
TI12064 | 2000-F12-PID-PR-10001 | F12CG401 Outr Ecc Upper | Analogue | A_HH | 60 | ℃ | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | B
TI12065 | 2000-F12-PID-PR-10001 | F12CG401 Outr Ecc Ring | Analogue | A_Hi | 54 | ℃ | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate Lubrication Oil temperature & Oil Chiller circuit. | B
TI12065 | 2000-F12-PID-PR-10001 | F12CG401 Outr Ecc Ring | Analogue | A_HH | 60 | ℃ | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | B
TI12066 | 2000-F12-PID-PR-10001 | F12CG401 Outr Ecc Lower | Analogue | A_Hi | 54 | ℃ | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate Lubrication Oil temperature & Oil Chiller circuit. | B
TI12066 | 2000-F12-PID-PR-10001 | F12CG401 Outr Ecc Lower | Analogue | A_HH | 60 | ℃ | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | B
TI12067 | 2000-F12-PID-PR-10001 | F12CG401 C/Shaft OB Brg | Analogue | A_Hi | 54 | ℃ | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate Lubrication Oil temperature & Oil Chiller circuit. | B
TI12067 | 2000-F12-PID-PR-10001 | F12CG401 C/Shaft OB Brg | Analogue | A_HH | 60 | ℃ | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | B
TI12068 | 2000-F12-PID-PR-10001 | F12CG401 C/Shaft IB Brg | Analogue | A_Hi | 54 | ℃ | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate Lubrication Oil temperature & Oil Chiller circuit. | B
TI12068 | 2000-F12-PID-PR-10001 | F12CG401 C/Shaft IB Brg | Analogue | A_HH | 60 | ℃ | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | B
FI12071 | 2000-F12-PID-PR-10001 | F12CG401 Outer Ecc Lube | Analogue | A_LL | 50 | LPM | 5 | Mask when F12-PO-404/405 is Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | C
FI12071 | 2000-F12-PID-PR-10001 | F12CG401 Outer Ecc Lube | Analogue | A_Lo | 86 | LPM | 5 | Mask when F12-PO-404/405 is Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Equipment tripped. Operator to investigate & restart if safe to do so. | C
FI12072 | 2000-F12-PID-PR-10001 | F12CG401 Upper Ecc. Lube | Analogue | A_LL | 7.5 | LPM | 5 | Mask when F12-PO-404/405 is Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate Duty Lubrication Oil Pump. | C
FI12072 | 2000-F12-PID-PR-10001 | F12CG401 Upper Ecc. Lube | Analogue | A_Lo | 13.5 | LPM | 5 | Mask when F12-PO-404/405 is Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Equipment tripped. Operator to investigate & restart if safe to do so. | C
FI12073 | 2000-F12-PID-PR-10001 | F12CG401 Pinion Lube | Analogue | A_LL | 7.5 | LPM | 5 | Mask when F12-PO-404/405 is Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate Duty Lubrication Oil Pump. | C
FI12073 | 2000-F12-PID-PR-10001 | F12CG401 Pinion Lube | Analogue | A_Lo | 13.5 | LPM | 5 | Mask when F12-PO-404/405 is Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Equipment tripped. Operator to investigate & restart if safe to do so. | C
FI12074 | 2000-F12-PID-PR-10001 | F12CG401 C/Shaft Lube | Analogue | A_LL | 7.5 | LPM | 5 | Mask when F12-PO-404/405 is Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate Duty Lubrication Oil Pump. | C
FI12074 | 2000-F12-PID-PR-10001 | F12CG401 C/Shaft Lube | Analogue | A_Lo | 13.5 | LPM | 5 | Mask when F12-PO-404/405 is Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Equipment tripped. Operator to investigate & restart if safe to do so. | C
FI12075 | 2000-F12-PID-PR-10001 | F12CG401 Inner Ecc. Lube | Analogue | A_LL | 50 | LPM | 5 | Mask when F12-PO-404/405 is Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate Duty Lubrication Oil Pump. | C
FI12075 | 2000-F12-PID-PR-10001 | F12CG401 Inner Ecc. Lube | Analogue | A_Lo | 86 | LPM | 5 | Mask when F12-PO-404/405 is Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Equipment tripped. Operator to investigate & restart if safe to do so. | C
FI12079 | 2000-F12-PID-PR-10001 | F12BW401 Seal Blower | Analogue | A_LL | 34 | m3/hr | 5 | Mask when F12-CG-401 is Not Running and F12-BW-401 is Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate. | 0
FI12079 | 2000-F12-PID-PR-10001 | F12BW401 Seal Blower | Analogue | A_Lo | 60 | m3/hr | 5 | Mask when F12-CG-401 is Not Running and F12-BW-401 is Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate. | B
TI12080 | 2000-F12-PID-PR-10001 | F12LU401 Hyd Oil Resvr | Analogue | A_HH | 60 | ℃ | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate cause of high hydraulic oil temperature. | C
TI12080 | 2000-F12-PID-PR-10001 | F12LU401 Hyd Oil Resvr | Analogue | A_LL | 21 | ℃ | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate operation of heaters. | C
TI12080 | 2000-F12-PID-PR-10001 | F12LU401 Hyd Oil Resvr | Analogue | A_Lo | 27 | ℃ | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate operation of heaters. | C
LALL12081 | 2000-F12-PID-PR-10001 | F12LU401 HydOilResvrLL | Digital | Closed (Low Low) |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | 2
LAL12081 | 2000-F12-PID-PR-10001 | F12LU401 HydOilResvrLo | Digital | Closed (Low) |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Hydraulic oil level low. Operator to investigate. | 2
PDAH12088 | 2000-F12-PID-PR-10001 | F12LU401 HydFilterDiffHi | Digital | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to changeout filter and/or utilise standby filter. | 2
PDAHH12088 | 2000-F12-PID-PR-10001 | F12LU401 HydFilterDiffHH | Digital | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to change-out lube filter. | 2
WI12097 | 2000-F12-PID-PR-10001 | F12LU402 Grease Drum | Analogue | A_Lo | 44 | kg | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to organise grease drum change-out. Require's downtime of Primary Crusher 2. | 2
WI12097 | 2000-F12-PID-PR-10001 | F12LU402 Grease Drum | Analogue | A_LL | 44 | kg | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to organise grease drum change-out. Require's downtime of Primary Crusher 2. | 2
TI12110 | 2000-F12-PID-PR-10001 | F12LU401 Lube Tank | Analogue | A_LL | 21 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate heater operation. Plant tripped. | B
TI12110 | 2000-F12-PID-PR-10001 | F12LU401 Lube Tank | Analogue | A_Lo | 27 | ℃ | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate correct operation of heaters and/or chiller. | B
TI12110 | 2000-F12-PID-PR-10001 | F12LU401 Lube Tank | Analogue | A_HH | 60 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate chiller and heater operation. | 2
TI12110 | 2000-F12-PID-PR-10001 | F12LU401 Lube Tank | Analogue | A_Hi | 60 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate chiller and heater operation. | 2
LALL12111 | 2000-F12-PID-PR-10001 | F12LU401 LubeOilResvrLL | Digital | Closed (Low Low) |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate Lubrication system for reservoir level and any loss of containment. | 2
LAL12111 | 2000-F12-PID-PR-10001 | F12LU401 LubeOilResvrLo | Digital | Closed (Low) |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate Lubrication system for reservoir level and any loss of containment. | 2
PI12118 | 2000-F12-PID-PR-10001 | F12PO404/405 Discharge | Analogue | A_Hi | 727 | kPa | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate cause of high lubrication pump discharge pressure (blocked filter, faulty PRV). | 0
PDAH12121 | 2000-F12-PID-PR-10001 | F12LU401 LubeFlterDiffHi | Digital | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate Lubrication Oil Filter & replacement. | 2
PDAHH12121 | 2000-F12-PID-PR-10001 | F12LU401 LubeFlterDiffHH | Digital | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to change-out lube filter. | 2
AAH12125 | 2000-F12-PID-PR-10001 | F12LU401 Return Moisture | Digital | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate Primary Crusher 2 Lubrication system for moisture in oil. | 2
TIC12127 | 2000-F12-PID-PR-10001 | F12CG401 Lube Oil Ctrl | Analogue | A_Hi | 43 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to investigate chiller & cooling water system operation. | 0
TIC12127 | 2000-F12-PID-PR-10001 | F12CG401 Lube Oil Ctrl | Analogue | A_HH | 46 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate chiller & cooling water system operation. | C
TI12128 | 2000-F12-PID-PR-10001 | F12LU401 Lube Return | Analogue | A_Hi | 55 | ℃ | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate Lubrication Heater operation and Oil Chiller operation. | B
TI12128 | 2000-F12-PID-PR-10001 | F12LU401 Lube Return | Analogue | A_HH | 60 | ℃ | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate Lubrication Heater operation, Oil Chiller operation and Primary Crusher 2 mechanical components. | B
HS12130ESTP | 2000-F12-PID-PR-10001 | F12LU401 EStop Active | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Plant Tripped | Logging | Equipment tripped due to E-Stop activated. Operator to investigate. | 2
PAL12231 | 2000-F12-PID-PR-10001 | F12PO436 G/Box | Digital | Activated |  |  | 3 | Mask if F12-PO-436 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Pump discharge less than 0.7 bar. Operator to check the oil cooler assembly. | 2
FALL12266 | 2000-F12-PID-PR-10003 | F12CU401 Inlet Water | Digital | Alarm |  |  | 3 | Duty F12PW425/426 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Duty F12-PW-425/426 Cooling Water Pump tripped. | 2
FAL12145 | 2000-F24-PID-PR-10009 | F12LU401 HX Cool Water | Digital | Open |  |  | 10 | Duty F12PW425/426 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate chiller and cooling system for Primary Crusher 2. | 1
LI12199 | 2000-F12-PID-PR-10001 | F12BN405 Disch Chamber 2 | Analogue | A_LL | 15 | % | 5 | Mask A_Lo and A_LoLo when LI12200 is healthy | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate & organise feed to Crusher. | C
LI12199 | 2000-F12-PID-PR-10001 | F12BN405 Disch Chamber 2 | Analogue | A_Lo | 20 | % | 5 | Mask A_Lo and A_LoLo when LI12200 is healthy | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | If Primary Crusher 2 is running, Operator to organise feed. | C
LI12200 | 2000-F12-PID-PR-10001 | F12BN405 Disch Chamber 1 | Analogue | A_LL | 15 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate & organise feed to Crusher. | B
LI12200 | 2000-F12-PID-PR-10001 | F12BN405 Disch Chamber 1 | Analogue | A_Lo | 20 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | If Primary Crusher 2 is running, Operator to organise feed. | B
LI12200 | 2000-F12-PID-PR-10001 | F12BN405 Disch Chamber 1 | Analogue | A_Hi | 85 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to halt further haul truck dumping into the ROM Bin until alarm cleared. Traffic lights are not in AUTO to prevent this condition. | C
LI12200 | 2000-F12-PID-PR-10001 | F12BN405 Disch Chamber 1 | Analogue | A_HH | 90 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate & restart if safe to do so. | C
LAH12201 | 2000-F12-PID-PR-10001 | F12BN405 Prim. Cr 2 LAH | Digital | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate Apron Feeder operation. | 2
LAL12202 | 2000-F12-PID-PR-10001 | F12HU401 Hydraulic Tank | Digital | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate Primary Crusher 2 Vault Door HPU tank level. | 2
ZIO12202 | 2000-F12-PID-PR-10001 | F12HU401 Door 1 | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Vault Door Open. | 2
ZIO12203 | 2000-F12-PID-PR-10001 | F12HU401 Door 2 | Digital | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Vault Door Open. | 2
ZIO12204 | 2000-F12-PID-PR-10001 | F12HU401 Door 3 | Digital | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Vault Door Open. | 2
ZIO12205 | 2000-F12-PID-PR-10001 | F12HU401 Door 4 | Digital | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Vault Door Open. | 2
PWA12221A | 2000-F12-PID-PR-10001 | F12FA401 P/W RHS | Digital | Activated |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Plant Tripped | Logging | Potential personnel injury. Operator to advise Shift Supervisor and urgently investigate. | 0
PWA12221B | 2000-F12-PID-PR-10001 | F12FA401 P/W LHS | Digital | Activated |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Plant Tripped | Logging | Potential personnel injury. Operator to advise Shift Supervisor and urgently investigate. | 0
SAL12222 | 2000-F12-PID-PR-10001 | F12FA401 Underspeed | Digital | Alarm |  |  | 0 | F12-FA-401 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate Apron Feeder operation. | 2
XA12224 | 2000-F12-PID-PR-10001 | F12FA401 Grease Cycle Sw | Digital | N_Activated |  |  | 10 | Mask if F12-LU-441 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Investigate source of low flow (insufficient grease level, leak in lines) and rectify immediately. Continue to run apron feeder until warning is active for 24 hours. | 0
LAL12225 | 2000-F12-PID-PR-10001 | F12FA401 Grease Level | Digital | Activated |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate lubrication tank level. Failure to rectify within 24 hours will result in apron feeder tripping. | 2
LAH12227 | 2000-F12-PID-PR-10001 | F12CH402 Blocked Chute | Digital | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
TI12228 | 2000-F12-PID-PR-10001 | F12FA401 Gearbox Sump | Analogue | A_HH | 90 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Gearbox overloaded. Apron feeder tripped. Check gearbox for faults or overloading. | 0
TI12229 | 2000-F12-PID-PR-10001 | F12FA401 Gearbox Bearing | Analogue | A_Hi | 60 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | High speed bearing temperature above 60C. Investigate source of high temperature. Continue to run apron feeder. | 0
TI12229 | 2000-F12-PID-PR-10001 | F12FA401 Gearbox Bearing | Analogue | A_HH | 90 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | High speed bearing temperature above 90C. Apron feeder motor tripped. Resolve source of high temperature. | 0
PDAH12230 | 2000-F12-PID-PR-10001 | F12PO436 Filter Delta | Digital | Activated |  |  | 3 | Mask if F12-PO-436 Not Running | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to manually change over the duty/standby filter inserts and replace the used filter insert. | 2
LI12260 | 2000-F12-PID-PR-10003 | F12TK423 Cooling Water | Analogue | A_LL | 20 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Cooling Water Pumps tripped. Operator to investigate top-up water actuated valve and/or organise manual water top-up if required. | 0
LI12260 | 2000-F12-PID-PR-10003 | F12TK423 Cooling Water | Analogue | A_Lo | 30 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to investigate if actuated cooling water tank top-up valve is in manual and/or faulty. Inaction will result in Primary Crusher 2 downtime. | 0
LI12260 | 2000-F12-PID-PR-10003 | F12TK423 Cooling Water | Analogue | A_Hi | 80 | % | 5 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | Operator to investigate if cooling water top-up valve is open and in manual and requires closing to prevent tank overflow. | 0
TI12261 | 2000-F12-PID-PR-10003 | F12TK423 Cooling Water | Analogue | A_Hi | 30 | ℃ | 5 | Mask when F12-PW-425 AND 426 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to check function of Primary Crusher 2 Chiller (F12-CU-401) and Chiller discharge temperature indicator process value. | 0
TI12267 | 2000-F12-PID-PR-10003 | F12CU401 Outlet Water | Analogue | A_Hi | 20 | ℃ | 5 | Mask when F12-PW-425 AND 426 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to check function of Primary Crusher 2 Chiller (F12-CU-401). | 0
XA12268 | 2000-F12-PID-PR-10003 | F12CU401 Chiller Fault | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Chiller tripped. Operator to investigate on package HMI. | 2
LAH12370 | 2000-F12-PID-PR-10001 | F12PS401 Crusher Sump | Digital | Alarm |  |  | 3 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | Spillage contained in bund. Operator to investigate operation of sump pump. | 2
PI12392 | 2000-F24-PID-PR-10012 | F12RA407 Outlet Pressure | Analogue | A_Lo | 600 | kPa | 5 | Mask A_Lo alarm when F24-CM-401, 402 AND 403 are stopped Mask A_Lo for 30 seconds during start up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate and initiate compressor changeover if alarm not cleared with fault finding. | 0
PI12392 | 2000-F24-PID-PR-10012 | F12RA407 Outlet Pressure | Analogue | A_Hi | 1000 | kPa | 5 | Mask A_Lo alarm when F24-CM-401, 402 AND 403 are stopped Mask A_Lo for 30 seconds during start up. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate and initiate line flushing if alarm not cleared with fault finding. | 0
F12BN401_DUMP | 2000-F12-PID-PR-10001 | F12BN401 2 Trucks Dump | Digital | Activated |  |  | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Immediate (<5 minutes) | Urgent | Operator to radio haul truck operators to cease approach and dumping for safety concerns. | 2
PWA12501A | 2000-F12-PID-PR-10002 | F12CV401 Tail P/W RHS | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Plant Tripped | Logging | Potential personnel injury. Operator to advise Shift Supervisor and urgently investigate. | 0
PWA12501B | 2000-F12-PID-PR-10002 | F12CV401 Tail P/W LHS | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Plant Tripped | Logging | Potential personnel injury. Operator to advise Shift Supervisor and urgently investigate. | 0
PWA12501C | 2000-F12-PID-PR-10002 | F12CV401 Head P/W RHS | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Plant Tripped | Logging | Potential personnel injury. Operator to advise Shift Supervisor and urgently investigate. | 0
PWA12501D | 2000-F12-PID-PR-10002 | F12CV401 Head P/W LHS | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Plant Tripped | Logging | Potential personnel injury. Operator to advise Shift Supervisor and urgently investigate. | 0
SAL12502 | 2000-F12-PID-PR-10002 | F12CV401 H/E Belt Speed | Digital | Alarm |  |  | 3 | F12-CV-401 Not Running and Mask on start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate cause of low speed trip on F12CV401. | 2
BDA12503C | 2000-F12-PID-PR-10002 | F12CV401 Head Drift RHS | Digital | Alarm |  |  | 3 | F12-CV-401 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
BDA12503D | 2000-F12-PID-PR-10002 | F12CV401 Head Drift LHS | Digital | Alarm |  |  | 3 | F12-CV-401 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
BDA12503A | 2000-F12-PID-PR-10002 | F12CV401 Tail Drift RHS | Digital | Alarm |  |  | 3 | F12-CV-401 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
BDA12503B | 2000-F12-PID-PR-10002 | F12CV401 Tail Drift LHS | Digital | Alarm |  |  | 3 | F12-CV-401 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
BDA12503E | 2000-F12-PID-PR-10002 | F12CV401 TakeUpDrift RHS | Digital | Alarm |  |  | 3 | F12-CV-401 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
BDA12503F | 2000-F12-PID-PR-10002 | F12CV401 TakeUpDrift LHS | Digital | Alarm |  |  | 3 | F12-CV-401 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
BRA12504 | 2000-F12-PID-PR-10002 | F12CV401 Belt Rip | Digital | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Belt rip. Operator to investigate and safely shutdown crushing plant. | 2
ZSA12506A | 2000-F12-PID-PR-10002 | F12CV401 Take-Up LHS | Digital | Alarm |  |  | 3 | F12-CV-401 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | F12CV401 tripped. Advise Field Operator / Maintenance team to investigate take up pulley immediately. | 2
ZSA12506B | 2000-F12-PID-PR-10002 | F12CV401 Take-Up RHS | Digital | Alarm |  |  | 3 | F12-CV-401 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | F12CV401 tripped. Advise Field Operator / Maintenance team to investigate take up pulley immediately. | 2
VI12507A | 2000-F12-PID-PR-10002 | F12CV401 Pulley1 | Analogue | A_Hi | 1 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of high vibration in drive pulley. | 0
VI12507A | 2000-F12-PID-PR-10002 | F12CV401 Pulley1 | Analogue | A_HH | 2 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate cause of excessive vibration in drive pulley. | 0
VI12507B | 2000-F12-PID-PR-10002 | F12CV401 Pulley2 | Analogue | A_Hi | 1 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of high vibration in drive pulley. | 0
VI12507B | 2000-F12-PID-PR-10002 | F12CV401 Pulley2 | Analogue | A_HH | 2 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate cause of excessive vibration in drive pulley. | 0
SAL12510 | 2000-F12-PID-PR-10002 | F12CV401 Under Speed | Digital | Alarm |  |  | 3 | F12-CV-401 Not Running and Mask on start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
LAH12511 | 2000-F12-PID-PR-10002 | F12CV401 Blocked Chute | Digital | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
XA12519 | 2000-F12-PID-PR-10002 | F12MG401 System Fault | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate system fault on F12MG401. Consult IOM. | 2
YIC12523 | 2000-F12-PID-PR-10001 | F12CG401 PSD p80 Ctrl | Analogue | A_Hi | 180 | mm | 5 | Mask when WIC12557 < P_Lo | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate OSS on Primary Crusher 2 and ensure it meets operational targets. | C
PDI12542 | 2000-F12-PID-PR-10002 | F12DC401 Pressure Delta | Analogue | A_LL | 300 | Pa | 5 | Mask if F12DC401 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Low delta alarm. Operator to investigate unit in-field. | C
PDI12542 | 2000-F12-PID-PR-10002 | F12DC401 Pressure Delta | Analogue | A_Lo | 800 | Pa | 5 | Mask if F12DC401 Not Running | None | Not Urgent (>30 minutes) | No Alarm | Logging Only. Stop Pulse Cleaning. | C
PDI12542 | 2000-F12-PID-PR-10002 | F12DC401 Pressure Delta | Analogue | A_Hi | 1300 | Pa | 5 | Mask if F12DC401 Not Running | None | Not Urgent (>30 minutes) | No Alarm | Logging Only. Start Pulse Cleaning. | C
PDI12542 | 2000-F12-PID-PR-10002 | F12DC401 Pressure Delta | Analogue | A_HH | 1800 | Pa | 5 | Mask if F12DC401 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | High delta alarm. Operator to investigate unit in-field. Compressed air supply may be compromised. Consult Vendor Functional Description for further details. | C
SAL12545 | 2000-F12-PID-PR-10002 | F12DC401 Rotary U/Speed | Digital | Alarm |  |  | 3 | F12-VR-401 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Operator to investigate cause of rotary valve underspeed switch being activated. | 2
PWA12552A | 2000-F12-PID-PR-10002 | F12CV402 Tail P/W RHS | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Plant Tripped | Logging | Potential personnel injury. Operator to advise Shift Supervisor and urgently investigate. | 0
PWA12552B | 2000-F12-PID-PR-10002 | F12CV402 Tail P/W LHS | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Plant Tripped | Logging | Potential personnel injury. Operator to advise Shift Supervisor and urgently investigate. | 0
PWA12552C | 2000-F12-PID-PR-10002 | F12CV402 Mid P/W (RHS) | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Plant Tripped | Logging | Potential personnel injury. Operator to advise Shift Supervisor and urgently investigate. | 0
PWA12552D | 2000-F12-PID-PR-10002 | F12CV402 Mid P/W LHS | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Plant Tripped | Logging | Potential personnel injury. Operator to advise Shift Supervisor and urgently investigate. | 0
SAL12553 | 2000-F12-PID-PR-10002 | F12CV402 Tail Underspeed | Digital | Alarm |  |  | 3 | F12-CV-402 Not Running and Mask on start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
SAL12554 | 2000-F12-PID-PR-10002 | F12CV402 Pulley U/Speed | Digital | Alarm |  |  | 0 | F12-CV-402 Not Running and Mask on start-up | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
BDA12555A | 2000-F12-PID-PR-10002 | F12CV402 Tail Drift RHS | Digital | Alarm |  |  | 3 | F12-CV-402 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
BDA12555B | 2000-F12-PID-PR-10002 | F12CV402 Tail Drift LHS | Digital | Alarm |  |  | 3 | F12-CV-402 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
BDA12555C | 2000-F12-PID-PR-10002 | F12CV402 Head Drift RHS | Digital | Alarm |  |  | 3 | F12-CV-402 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
BDA12555D | 2000-F12-PID-PR-10002 | F12CV402 Head Drift LHS | Digital | Alarm |  |  | 3 | F12-CV-402 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
BDA12555E | 2000-F12-PID-PR-10002 | F12CV402 TakeUpDrift RHS | Digital | Alarm |  |  | 3 | F12-CV-402 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
BDA12555F | 2000-F12-PID-PR-10002 | F12CV402 TakeUpDrift LHS | Digital | Alarm |  |  | 3 | F12-CV-402 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
BDA12555G | 2000-F12-PID-PR-10002 | F12CV402 Chute Drift RHS | Digital | Alarm |  |  | 3 | F12-CV-402 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
BDA12555H | 2000-F12-PID-PR-10002 | F12CV402 Chute Drift LHS | Digital | Alarm |  |  | 3 | F12-CV-402 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
BRA12556 | 2000-F12-PID-PR-10002 | F12CV402 Belt Rip Switch | Digital | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
WIC12557 | 2000-F12-PID-PR-10002 | F12CV402 Mass Ctrl | Analogue | A_LL | 1500 | tph | 5 | Mask when F12-CV-402 is NOT RUNNING. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Immediate (<5 minutes) | High | Operator to review cause of low crushing plant tonnage. | C
WIC12557 | 2000-F12-PID-PR-10002 | F12CV402 Mass Ctrl | Analogue | A_Lo | 1800 | tph | 5 | Mask when F12-CV-402 is NOT RUNNING. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review cause of low crushing plant tonnage. | C
WIC12557 | 2000-F12-PID-PR-10002 | F12CV402 Mass Ctrl | Analogue | A_Hi | 3200 | tph | 5 | Mask when F12-CV-402 is NOT RUNNING. | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to review cause of high crushing plant tonnage. | 0
ZSA12558A | 2000-F12-PID-PR-10002 | F12CV402 Takeup Left | Digital | Alarm |  |  | 3 | F12-CV-402 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | F12CV402 tripped. Advise Field Operator / Maintenance team to investigate take up pulley immediately. | 2
ZSA12558B | 2000-F12-PID-PR-10002 | F12CV402 Takeup Right | Digital | Alarm |  |  | 3 | F12-CV-402 Not Running | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | F12CV402 tripped. Advise Field Operator / Maintenance team to investigate take up pulley immediately. | 2
VI12560A | 2000-F12-PID-PR-10002 | F12CV402 Pulley1 | Analogue | A_Hi | 1 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of high vibration in drive pulley. | C
VI12560A | 2000-F12-PID-PR-10002 | F12CV402 Pulley1 | Analogue | A_HH | 2 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate cause of excessive vibration in drive pulley. | C
VI12560B | 2000-F12-PID-PR-10002 | F12CV402 Pulley2 | Analogue | A_Hi | 1 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of high vibration in drive pulley. | C
VI12560B | 2000-F12-PID-PR-10002 | F12CV402 Pulley2 | Analogue | A_HH | 2 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate cause of excessive vibration in drive pulley. | C
XA12563 | 2000-F12-PID-PR-10002 | F12DC401 System Fault | Digital | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
XA12567 | 2000-F12-PID-PR-10002 | F12MG402 System Fault | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate. | 2
TI12580A | 2000-F12-PID-PR-10002 | F12CV401 Mtr Phase U RTD | Analogue | A_Hi | 140 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of high winding temperature in-field. | 0
TI12580A | 2000-F12-PID-PR-10002 | F12CV401 Mtr Phase U RTD | Analogue | A_HH | 150 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate cause of high winding temperature in-field. | 0
TI12580B | 2000-F12-PID-PR-10002 | F12CV401 Mtr Phase V RTD | Analogue | A_Hi | 140 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of high winding temperature in-field. | 0
TI12580B | 2000-F12-PID-PR-10002 | F12CV401 Mtr Phase V RTD | Analogue | A_HH | 150 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate cause of high winding temperature in-field. | 0
TI12580C | 2000-F12-PID-PR-10002 | F12CV401 Mtr Phase W RTD | Analogue | A_Hi | 140 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of high winding temperature in-field. | 0
TI12580C | 2000-F12-PID-PR-10002 | F12CV401 Mtr Phase W RTD | Analogue | A_HH | 150 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate cause of high winding temperature in-field. | 0
TI12580D | 2000-F12-PID-PR-10002 | F12CV401 Mtr DE Bearing | Analogue | A_Hi | 90 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of high bearing temperature in-field. | 0
TI12580D | 2000-F12-PID-PR-10002 | F12CV401 Mtr DE Bearing | Analogue | A_HH | 95 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate cause of high bearing temperature in-field. | 0
TI12580E | 2000-F12-PID-PR-10002 | F12CV401 Mtr NDE Bearing | Analogue | A_Hi | 90 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of high bearing temperature in-field. | 0
TI12580E | 2000-F12-PID-PR-10002 | F12CV401 Mtr NDE Bearing | Analogue | A_HH | 95 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate cause of high bearing temperature in-field. | 0
TI12581A | 2000-F12-PID-PR-10002 | F12CV402 Mtr Phase U RTD | Analogue | A_Hi | 140 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of high winding temperature in-field. | 0
TI12581A | 2000-F12-PID-PR-10002 | F12CV402 Mtr Phase U RTD | Analogue | A_HH | 150 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate cause of high winding temperature in-field. | 0
TI12581B | 2000-F12-PID-PR-10002 | F12CV402 Mtr Phase V RTD | Analogue | A_Hi | 140 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of high winding temperature in-field. | 0
TI12581B | 2000-F12-PID-PR-10002 | F12CV402 Mtr Phase V RTD | Analogue | A_HH | 150 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate cause of high winding temperature in-field. | 0
TI12581C | 2000-F12-PID-PR-10002 | F12CV402 Mtr Phase W RTD | Analogue | A_Hi | 140 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of high winding temperature in-field. | 0
TI12581C | 2000-F12-PID-PR-10002 | F12CV402 Mtr Phase W RTD | Analogue | A_HH | 150 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate cause of high winding temperature in-field. | 0
TI12581D | 2000-F12-PID-PR-10002 | F12CV402 Mtr DE Bearing | Analogue | A_Hi | 90 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of high bearing temperature in-field. | 0
TI12581D | 2000-F12-PID-PR-10002 | F12CV402 Mtr DE Bearing | Analogue | A_HH | 95 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate cause of high bearing temperature in-field. | 0
TI12581E | 2000-F12-PID-PR-10002 | F12CV402 Mtr NDE Bearing | Analogue | A_Hi | 90 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of high bearing temperature in-field. | 0
TI12581E | 2000-F12-PID-PR-10002 | F12CV402 Mtr NDE Bearing | Analogue | A_HH | 95 | ℃ | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate cause of high bearing temperature in-field. | 0
LAH12582 | 2000-F12-PID-PR-10002 | F12CV402 Blocked Chute | Digital | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate cause of blocked chute on Stockpile Feed Conveyor. | 2
LAHH13001 | 2000-F13-PID-PR-10001 | F12SKP401 Stockpile 2 | Digital | Alarm |  |  | 3 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Plant Tripped | Logging | Equipment tripped. Operator to investigate & safely shutdown crushing plant. | 2
LI13002 | 2000-F13-PID-PR-10001 | F12SKP401 Stockpile 2 | Analogue | A_Hi | 80 | % | 5 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operator to investigate wet plant status and decide whether to cease crushing. | B
LI13002 | 2000-F13-PID-PR-10001 | F12SKP401 Stockpile 2 | Analogue | A_HH | 90 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate wet plant status. Crushing plant production losses. | B
LI13002 | 2000-F13-PID-PR-10001 | F12SKP401 Stockpile 2 | Analogue | A_LL | 20 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Operator to investigate cause of low-low stockpile level. Crushing circuit in maintenance? Any emergency reserves? | C
LI13002 | 2000-F13-PID-PR-10001 | F12SKP401 Stockpile 2 | Analogue | A_Lo | 30 | % | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to investigate cause of low stockpile level. Crushing circuit in maintenance? Any emergency reserves? | C
F12DCS401_PS2 | 2000-F12-PID-PR-10001 | F12 DCS Pwr Healthy | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 2
F12SW001_PS | 2000-F12-PID-PR-10002 | F12CB Shunt Trip | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate in-field. | 2
F12SW001_PS1 | 2000-F12-PID-PR-10001 | F12SWR P1 Healthy | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 2
F12SW001_PS2 | 2000-F12-PID-PR-10001 | F12SWR P2 Healthy | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 2
F12BC001_FL1 | 2000-F12-PID-PR-10001 | F12Mains Fail | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate in-field. | 2
F12BC001_FL2 | 2000-F12-PID-PR-10001 | F12Char Batt Fail | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate in-field. | 2
F12BC001_FL4 | 2000-F12-PID-PR-10001 | F12Char Earth Fault | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate in-field. | 2
F12FIP001_ISL | 2000-F12-PID-PR-10001 | F12SwRoom Isolate | Digital | Alarm |  |  | 0 |  | Financial3: Loss equivalent greater than 6 hours production. Repairs costing >$500k | Rapid (>5 to <15 minutes) | Urgent | Fire alarm. Follow site specific Fire Emergency Plan. | 2
F12RIO001_PS1 | 2000-F12-PID-PR-10001 | F12RIO1 P1 Healthy | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 2
F12RIO001_PS2 | 2000-F12-PID-PR-10001 | F12RIO1 P2 Healthy | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 2
F12RIO002_PS1 | 2000-F12-PID-PR-10001 | F12RIO2 P1 Healthy | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 2
F12RIO002_PS2 | 2000-F12-PID-PR-10001 | F12RIO2 P2 Healthy | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Electrician to investigate | 2
XA12557 | 2000-F12-PID-PR-10002 | F12WD402 Weight Alarm | Digital | Alarm |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Fault with Weightometer. Operator to investigate in field. | 2
F12SW101_SD | 2000-F12-PID-PR-10001 | F12SW101 Surge Diverter | Digital | Alarm |  |  | 0 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Switchroom tripped. Electrician to investigate | 2
F12SW101_Q1CL | 2000-F12-PID-PR-10001 | F12SW101 Mains CB Closed | Digital | Alarm |  |  | 0 |  | None | Not Urgent (>30 minutes) | No Alarm | Switchroom tripped. Electrician to investigate | 2
F12SW101_Q1OP | 2000-F12-PID-PR-10001 | F12SW101 Mains CB Trip | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | SWB tripped. Electrician to investigate/ to Confirm manual generator changeover in operation | 2
F12SW101_Q2CL | 2000-F12-PID-PR-10001 | F12SW101 Gen CB Closed | Digital | Alarm |  |  | 0 |  | None | Not Urgent (>30 minutes) | No Alarm | Switchroom tripped. Electrician to investigate | 2
F12SW101_Q2OP | 2000-F12-PID-PR-10001 | F12SW101 Gen CB Trip | Digital | Alarm |  |  | 0 |  | None | Not Urgent (>30 minutes) | No Alarm | Switchroom tripped. Electrician to investigate | 2
LAHH12013 | 2000-F12-PID-PR-10001 | F12GE101 Fuel Level | Digital | Alarm |  |  | 0 |  | Environmental2: Minor on-site environmental impact, reportable to regulators. | Immediate (<5 minutes) | Urgent | Operator to cease re-fuelling immediately, likely diesel spillage. Operator to investigat in-field and respond in-line with company combustible material spillage protocol. | 2
LAH12013 | 2000-F12-PID-PR-10001 | F12GE101 Fuel Level | Digital | Alarm |  |  | 0 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Rapid (>5 to <15 minutes) | Low | High fuel level in generator fuel reservoir. Operator to radio local field operator to cease re-fuelling. | 2
LAL12013 | 2000-F12-PID-PR-10001 | F12GE101 Fuel Level | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Rapid (>5 to <15 minutes) | Low | Operational risk for backup power. Operator to organise re-fuelling. | 2
XA12562 | 2000-F12-PID-PR-10002 | F12DC401 Alarm | Digital | Alarm |  |  | 0 |  | Environmental1: Localised environmental impact, contained, with no regulatory reporting | Prompt (>15 to <30 minutes) | Low | Operator to investigate dust collector unit in-field. Likely issue with bag cleaning. | 1
TI12507B | 2000-F12-PID-PR-10002 | F12CV401 Pulley2 | Analogue | A_Hi | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect pulley in-field. | 1
TI12507B | 2000-F12-PID-PR-10002 | F12CV401 Pulley2 | Analogue | A_HH | 70 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Conveyor stopped. Operator to inspect pulley in-field. | 1
TI12560B | 2000-F12-PID-PR-10002 | F12CV402 Pulley2 | Analogue | A_Hi | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect pulley in-field. | 1
TI12560B | 2000-F12-PID-PR-10002 | F12CV402 Pulley2 | Analogue | A_HH | 70 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Conveyor stopped. Operator to inspect pulley in-field. | 1
PDAH12019B | 2000-F12-PID-PR-10001 | F12RB401 HPU Flilter | Digital | Activated |  |  | 3 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to organise filter change-out or utilise standby filter (if fitted). | 2
TI12507A | 2000-F12-PID-PR-10002 | F12CV401 Pulley1 | Analogue | A_Hi | 60 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect pulley in-field. | 1
TI12507A | 2000-F12-PID-PR-10002 | F12CV401 Pulley1 | Analogue | A_HH | 70 | °C | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Conveyor stopped. Operator to inspect pulley in-field. | 1
TI12560A | 2000-F12-PID-PR-10002 | F12CV402 Pulley1 | Analogue | A_Hi | 1 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Rapid (>5 to <15 minutes) | High | Operator to inspect pulley in-field. | 1
TI12560A | 2000-F12-PID-PR-10002 | F12CV402 Pulley1 | Analogue | A_HH | 2 | mm/s | 5 |  | Financial2: Loss equivalent greater than 1 hour and up to 6 hours production. Repairs costing $50k-$500k. | Plant Tripped | Logging | Conveyor stopped. Operator to inspect pulley in-field. | 1
ZAC12014 | N/A | F12TR001 415VMCCDoor CL | Digital | Alarm |  |  | 0 |  | Personnel2: Restricted Work Injury, Signficant, reversible health effect with potential to result in a medical treatment. | Immediate (<5 minutes) | Urgent | Restricted work area potential safety breach/issue | 2
F12SW012_HTY | N/A | F12SW012 Fuse Healthy | Digital | Alarm |  |  | 0 |  | Financial1: Loss equivalent up to 1 hour production. Repairs costing <$50,000 | Prompt (>15 to <30 minutes) | Low | Operator to investigate in-field. | 2